## F-1
Gallons of Water Pumped, Sold and Unaccounted For | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida (618-Jansen) | [8 empty] | Page 1 of 1
Docket No.: 060253-WS | [8 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2005
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
[10 empty] | Unaccounted |  | %
Month/ |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water |  | Unaccounted
Year |  | Pumped |  | Purchased |  | Sold |  | Uses |  | (1)+(2)-(3)-(4) |  | For Water
_ |  | _ |  | _ |  | _ |  | _ |  | _ |  | _
2005-01-01 |  | 1.902 |  | 0 |  | 2.13 |  | 0.003 |  | -0.231 |  | -12.15%
2005-02-01 |  | 1.892 |  | 0 |  | 1.805 |  | 0.018 |  | 0.069 |  | 3.647%
2005-03-01 |  | 1.883 |  | 0 |  | 1.867 |  | 0.008 |  | 0.008 |  | 0.4249%
2005-04-01 |  | 2.468 |  | 0 |  | 2.171 |  | 0.005 |  | 0.292 |  | 11.83%
2005-05-01 |  | 2.693 |  | 0 |  | 2.365 |  | 0 |  | 0.328 |  | 12.18%
2005-06-01 |  | 1.831 |  | 0 |  | 2.133 |  | 0.003 |  | -0.305 |  | -16.66%
2005-07-01 |  | 1.982 |  | 0 |  | 1.929 |  | 0.003 |  | 0.05 |  | 2.523%
2005-08-01 |  | 2.229 |  | 0 |  | 1.969 |  | 0.003 |  | 0.257 |  | 11.53%
2005-09-01 |  | 2.147 |  | 0 |  | 2.186 |  | 0.003 |  | -0.042 |  | -1.956%
2005-10-01 |  | 2.487 |  | 0 |  | 1.56 |  | 0.003 |  | 0.924 |  | 37.15%
2005-11-01 |  | 2.024 |  | 0 |  | 1.729 |  | 0.003 |  | 0.292 |  | 14.43%
2005-12-01 |  | 2.026 |  | 0 |  | 2.051 |  | 0.003 |  | -0.028 |  | -1.382%
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 25.564 |  | 0 |  | 23.895 |  | 0.055 |  | 1.614 |  | 6.314%
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)

## F-2
Gallons of Wastewater Treated | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida (618-Jansen) | [8 empty] | Page 1 of 1
Docket No.: 060253-WS | [8 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2005
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | (Name) |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2005-01-01 | [9 empty] | 0 |  | 0
2005-02-01 | [9 empty] | 0 |  | 0
2005-03-01 | [9 empty] | 0 |  | 0
2005-04-01 |  |  | Not applicable - water only system | [6 empty] | 0 |  | 0
2005-05-01 | [9 empty] | 0 |  | 0
2005-06-01 | [9 empty] | 0 |  | 0
2005-07-01 | [9 empty] | 0 |  | 0
2005-08-01 | [9 empty] | 0 |  | 0
2005-09-01 | [9 empty] | 0 |  | 0
2005-10-01 | [9 empty] | 0 |  | 0
2005-11-01 | [9 empty] | 0 |  | 0
2005-12-01 | [9 empty] | 0 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 0 | [7 empty] | 0 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =

## F-3
Water Treatment Plant Data | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (618-Jansen) | [6 empty] | Schedule F-3
Docket No.: 060253-WS | [6 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [7 empty] | * | 310000
on the DEP operating or construction permit, provide an explanation.
[* Per DEP, limited by well capacity]
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2005-10-25 | 307000
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2005-08-05 | 87000
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2005-08-28 | 90000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2005-08-29 | 90000
| these days. | [6 empty] | (4) | 2005-08-17 | 100000
[8 empty] | (5) | 2005-08-01 | 150000
[9 empty] | AVERAGE | 103400
[9 empty] | Max Month | 71903.2258
4 | Average Daily Flow | [7 empty] | Annual | 70038.3562
5 | Required Fire Flow | [8 empty] | None
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F-4
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (618-Jansen) | [8 empty] | Schedule F-4
Docket No.: 060253-WS | [8 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
|  | Not applicable - water only system | [6 empty] | _ |  | _
1. | Plant Capacity
The hydraulic rated capacity. If different from that shown
on the DEP operating or construction permit, provide an explanation.
2. | Average Daily Flow Max Month (a)
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F-5
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida (618-Jansen) | [5 empty] | Schedule F-5
Docket No.: 060253-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm | [5 empty] | 430 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm | [5 empty] | 190 | gpm
| Ground storage capacity, gal. | [5 empty] | 0 | gallons
| Usable ground storage (90%), gal. | [5 empty] | 0 | gallons
| Hydropneumatic storage capacity, gal. | [5 empty] | 6000 | gallons
| Usable hydropneumatic storage capacity (33.33%), gal. | [5 empty] | 2000 | gallons
| Total usable storage, gal. | [5 empty] | 2000 | gallons
| High service pumping capacity, gpm | [5 empty] | 0 | gpm
| Average day demand, maximum month | [5 empty] | 71903.2258 | gpd
| Maximum day, maximum month demand, | [5 empty] | 150000 | gpd
| Peak hour demand = 2 x max day | [5 empty] | 300000 | gpd
|  |  | or |  |  |  | 208.3333 | gpm
| Fire flow requirement | [5 empty] | 0 | gpd
| Unaccounted for water |  |  | 6.314% | of water pumped |  | 4421.9178 | gpd, avg
| Acceptable unaccounted for |  |  | 12.5% |  |  | 8754.7945 | gpd, avg
| Excess unaccounted for | [5 empty] | 0 | gpd, avg
Used & Useful Analysis:
Used & useful was last set for this system in Docket No. 020071-WS. The Commission found the system
to be 100% used & useful, as it had in past cases. There have been no significant changes in the system.
The service area is built out.
This system treats water by iron sequestration and chlorination. The only storage is in two hydropneumatic tanks
and there is no high service pumping. All demands must be met by well pumping capacity. Used and useful is
therefore determined on the basis of instantaneous demand, using peak hour demand as a proxy. For this system,
all components are considered together for purposes of determining used & useful. The system is built out and is
100% used & useful.
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: | [5 empty] | 100%
| A = | Peak demand |  |  |  |  | 208.3333 | gpm
| B = | Property needed to serve five years after TY |  |  |  |  | 0
| C = | Fire flow demand |  |  |  |  | 0
| D = | Excess Unaccounted for water |  |  |  |  | 0
| E = | Firm Reliable Capacity |  |  |  |  | 190 | gpm
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts,
as well as the land, structures and distribution reservoir accounts.

## F-6
Used and Useful Calculations |  | FPSC
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida (618-Jansen) |  | Schedule F-6
Docket No.: 060253-WS |  | Page 1 of 1
Test Year Ended: December 31, 2005 |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Not applicable - water only system

## F-7
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida (618-Jansen) | [5 empty] | Schedule F-7
Docket No.: 060253-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution System
Used & useful was last set for this system in Docket No. 020071-WS. The Commission found the distribution
system to be 100% used & useful, as it had in past cases. There have been no significant changes in the system.
The service area is built out and the distribution system remains 100% used & useful..

## F-8
Margin Reserve Calculations |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida (618-Jansen) |  | Schedule F-8
Docket No.: 060253-WS |  | Page 1 of 1
Test Year Ended: December 31, 2005 |  | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Not applicable - system built out. See Docket No. 020071-WS

## F-9
Equivalent Residential Connections - Water | [7 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (618-Jansen) | [7 empty] | Schedule F-9
Docket No.: 060253-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2001 | 246 | 244 |  | 245 |  | 27608842 | 112689.151 | 27781402 |  | 246.5313
2 | 2002 | 244 | 247 |  | 245.5 |  | 28159773 | 114703.7597 | 28294423 |  | 246.6739 | 0.05784%
3 | 2003 | 247 | 250 |  | 248.5 |  | 25630580 | 103141.167 | 25864390 |  | 250.7669 | 1.659%
4 | 2004 | 250 | 250 |  | 250 |  | 27517575 | 110070.3 | 27647775 |  | 251.1829 | 0.1659%
5 | 2005 | 250 | 252 |  | 251 |  | 23484833 | 93565.0717 | 23732443 |  | 253.6464 | 0.9808%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 0.7159%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 244.1385 |  | 1 | 246.5313
[6 empty] | X Coefficient: |  | 1.8739 |  | 2 | 246.6739
[6 empty] | R^2: |  | 0.92189 |  | 3 | 250.7669
[10 empty] | 4 | 251.1829
[10 empty] | 5 | 253.6464
[10 empty] | 10 | 262.8777

## F-10
Equivalent Residential Connections - Wastewater |  |  |  |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida (618-Jansen) | [6 empty] | Schedule F-10
Docket No.: 060253-WS | [6 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9)
|  | SFR Customers |  |  | SFR | Gallons/ | Total | Total | Annual
Line |  |  |  |  | Gallons | SFR | Gallons | ERCs | % Incr.
No. | Year | Beginning | Ending | Average | Sold | (5)/(4) | Sold | (7)/(6) | in ERCs
1 | TY-4
2 | TY-3 |  | Not applicable - water only system
3 | TY-2
4 | TY-1
5 | TY
Average Growth Through 5-Year Period (Col. 8)