1

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

DOCKET NO. 070183-WS

3

In the Matter of:

4

PROPOSED ADOPTION OF RULE 25-30.4325,

5   F.A.C., WATER TREATMENT PLANT USED

AND USEFUL CALCULATIONS.

6   _____________________________________/

7

8

9             ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

10               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

11

12                              VOLUME 1

Pages 1 through 175

13

PROCEEDINGS:        HEARING

14

BEFORE:             CHAIRMAN MATTHEW M. CARTER, II

15                       COMMISSIONER LISA POLAK EDGAR

COMMISSIONER KATRINA J. McMURRIAN

16                       COMMISSIONER NANCY ARGENZIANO

COMMISSIONER NATHAN A. SKOP

17

DATE:               Tuesday, January 22, 2008

18

TIME:               Commenced at 9:30 a.m.

19

PLACE:              Betty Easley Conference Center

20                       Room 148

4075 Esplanade Way

21                       Tallahassee, Florida

22   REPORTED BY:        LINDA BOLES, RPR, CRR

Official FPSC Reporter

23                       (850) 413-6734

24

25

FLORIDA PUBLIC SERVICE COMMISSION

2

1   APPEARANCES:

2             MARTIN S. FRIEDMAN, ESQUIRE, Rose Law Firm, 2180 West

3   State Road 434, Suite 2118, Longwood, Florida 32779, appearing

4   on behalf of Utilities, Inc. of Florida.

5             KENNETH A. HOFFMAN, ESQUIRE, and MARSHA E. RULE,

6   ESQUIRE, Rutledge Law Firm, Post Office Box 551, Tallahassee,

7   Florida 32302-0551, appearing on behalf of Aqua Utilities

8   Florida, Inc.

9             STEPHEN C. REILLY, ESQUIRE, Office of Public Counsel,

10   c/o The Florida Legislature, 111 West Madison Street, Room 812,

11   Tallahassee, Florida 32399-1400, appearing on behalf of the

12   Citizens of the State of Florida.

13             ROSANNE GERVASI, ESQUIRE, and RALPH JAEGER, ESQUIRE,

14   FPSC General Counsel's Office, 2540 Shumard Oak Boulevard,

15   Tallahassee, Florida 32399-0850, appearing on behalf of the

16   Commission Staff.

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

3

1                              I N D E X

2                              WITNESSES

3

NAME:                                              PAGE NO.

4

5   ANDREW T. WOODCOCK

6        Direct Examination by Mr. Reilly                 30

Prefiled Direct Testimony Inserted               39

7        Cross Examination by Mr. Hoffman                 68

Cross Examination by Mr. Friedman                90

8        Cross Examination by Ms. Gervasi                 98

Redirect Examination by Mr. Reilly              114

9

10   JOHN F. GUASTELLA

11        Direct Examination by Mr. Hoffman               119

Prefiled Direct Testimony Inserted              122

12        Cross Examination by Mr. Reilly                 142

Cross Examination by Mr. Friedman               150

13        Cross Examination by Mr. Jaeger                 151

Redirect Examination by Mr. Hoffman             171

14

15   CERTIFICATE OF REPORTER                              175

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

4

1                              EXHIBITS

2   NUMBER:                                        ID.    ADMTD.

3   1    Comprehensive Exhibit List                 17      29

4   2    ATW-1                                      37     118

5   4    Attachment 1 to John F. Guastella         121     173

prefiled

6

5    JFG-1                                     121     173

7

6    JFG-2                                     121     173

8

7    JFG-3                                     121     173

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

5

1                         P R O C E E D I N G S

2             CHAIRMAN CARTER:  Good morning.  I call this hearing

3   to order.  I'd ask staff to please read the notice.

4             MS. GERVASI:  Pursuant to notice, this time and place

5   have been set for a full evidentiary hearing in Docket Number

6   070183-WS, In re:  Proposed Adoption of Rule 25-30.4325,

7   Florida Administrative Code, Water Treatment Plant Used and

8   Useful Calculations.

9             CHAIRMAN CARTER:  Okay.  Let us now take appearances.

10             MR. FRIEDMAN:  My name is Martin Friedman of the law

11   firm of Rose, Sundstrom & Bentley, and we represent Utilities,

12   Inc. in this matter.  Utilities, Inc. does have two

13   representatives present, Mr. Rick Durham, who is the Regional

14   Vice President of Operations, and I think everybody knows John

15   Williams, who is the Director of Communications.  Thank you.

16             CHAIRMAN CARTER:  Mr. Reilly.

17             MR. REILLY:  Steve Reilly with the Office of Public

18   Counsel on behalf of the ratepayers.  I also have Andy

19   Woodcock, who is our engineer and the witness that we're

20   sponsoring today.

21             CHAIRMAN CARTER:  Okay.

22             MR. HOFFMAN:  Good morning, Mr. Chairman,

23   Commissioners.  My name is Ken Hoffman.  To my left is Marsha

24   Rule.  We are with Rutledge, Ecenia, Purnell & Hoffman here in

25   Tallahassee.  We're here this morning on behalf of Aqua

FLORIDA PUBLIC SERVICE COMMISSION

6

1   Utilities Florida.

2             CHAIRMAN CARTER:  Okay.

3             MS. GERVASI:  And Rosanne Gervasi and Ralph Jaeger

4   appearing on behalf of the Commission.

5             CHAIRMAN CARTER:  Okay.  Staff, any preliminary

6   matters?

7             MS. GERVASI:  Yes, sir.  There are a few preliminary

8   matters, the first of which is an outstanding motion that needs

9   to be ruled on.  This is Public Counsel's motion to file

10   revised recommended Rule 25-30.4325, F.A.C.  Public Counsel

11   filed the motion on January the 9th.  Aqua Utilities filed a

12   response in opposition to the motion.  Oral argument on the

13   motion was not requested.  Neither party requested oral

14   argument.  Nevertheless, you may allow oral argument in your

15   discretion or you may rule on the motion as presiding officer

16   or have the full Commission rule, at your pleasure.

17             CHAIRMAN CARTER:  Okay.  Let me do this as a -- I

18   think I'm -- Commissioners, I think I'm going to handle this as

19   the presiding officer.  Even though the parties did not request

20   oral argument on the motion, I think I'll give each side five

21   minutes to be heard on that and then I'll make my ruling then

22   on the preliminary matter about the outstanding motion.

23             I believe, Mr. Reilly, you'll be on first.

24             MR. REILLY:  Okay.  Thank you.  You'll remember at

25   the prehearing conference the citizens indicated a desire to

FLORIDA PUBLIC SERVICE COMMISSION

7

1   file a revised ATW-2 which incorporated all of our suggested

2   changes.  It is our belief that this would be a great aid to

3   the Commissioners and the parties in knowing the updated

4   version of our suggested changes all in one easy reference.  My

5   suggestion, however, was met with some resistance by both the

6   utilities and staff until they could review the ATW-2 and see

7   exactly what it did provide.  Aqua suggested I go ahead and

8   file a motion requesting it and provide copies so they'd have

9   plenty of time before the hearing to look at our proposed

10   changes, which I did.  I provided a clean copy and I also

11   provided a strike and add version so they could see, you know,

12   how the revised rule, revised proposed rule was different than

13   the other.  They -- I agreed to file this motion by the end of

14   business on January 9, which we did do.

15             I also pointed out at the prehearing conference that

16   I believe all of the changes were in response to utility and

17   staff's testimony and believed for the most part brought OPC's

18   positions actually closer to the rule's actual language.  So I

19   did file my motion on the 9th.  The only party who filed an

20   objection to our motion was Aqua, and in their response they

21   argued very vigorously that the revised rule was tardy, it was

22   procedurally inappropriate, it would irrevocably prejudice Aqua

23   and the other participants, that it constituted an 11th hour

24   revised rule, that it was a last-minute set of revised rule

25   proposals, that it really constituted a new set of OPC

FLORIDA PUBLIC SERVICE COMMISSION

8

1   proposals not reflected, not reflected in OPC's prefiled

2   testimony and exhibits, and that the revised recommended rule

3   provided sweeping revisions to its originally proposed rule and

4   that Aqua would be severely prejudiced by this belated

5   introduction.  We respectfully argue that all these arguments

6   are without merit.

7             The filing of this revised rule is neither untimely

8   or prejudicial.  Every single change included in revised ATW-2,

9   our revised proposed rule, is fully supported, fully supported

10   by timely filed rebuttal testimony, with the exception of two

11   things, and these were two things that were suggested to staff

12   in our pre prehearing conference that we held before the actual

13   prehearing conference.  These two suggestions were that, and

14   this came, actually came from staff, they said our putting, and

15   I'll get the exact language here, our Paragraphs 8 and 9 should

16   be reversed.  So there was no change in substance.  It was just

17   change in order.  And these two were at the end of our proposed

18   rule that dealt with, let me see, 8 and 9.  They felt it would

19   be more appropriate to have firm reliable capacity of high

20   service pumping before the actual paragraph that dealt with the

21   used and usefulness of high service pumping.  They suggested

22   that that would be a more natural order of the paragraphs.

23             The second involved no change in position but the

24   need to clarify the paragraph on how to calculate the used and

25   useful of high service pumping.  "The used and useful of high

FLORIDA PUBLIC SERVICE COMMISSION

9

1   service pumping is determined" -- this is our existing

2   language, (9), "The used and usefulness of high service pumping

3   is determined by dividing the peak demand for high service

4   pumping as defined in this rule by the firm reliable capacity

5   of the high service pumps."  So that was our original language.

6   That language did not change in any way.

7             There's no change in position.  The problem came was

8   that with that language as defined in this rule -- the thing

9   which was earlier defined in this rule only went so far, and

10   this is where you'll see in our rule, it's (1)(d) where it does

11   speak about peak demand for water treatment includes.  And

12   so -- and that's no change.  We keep that exactly like it is.

13   But what we failed to do in this, in this earlier definition in

14   (1)(f) of our recommended rule, it does not explain how to

15   calculate peak hour demand and maximum day demand.  So it was

16   just an omission of being more complete with high service

17   pumping as we had been fully complete with treatment.

18             So it's not an 11th hour change of position because

19   we propose to make exactly the same calculations.  This is a

20   very important point, we propose to make the exact same

21   calculations of how to calculate these things that we are

22   recommending for calculating peak hour demand and maximum day

23   demand for treatment just to make it completely consistent.  So

24   it's just actually literally filling in a little bit and

25   showing that we're completely consistent and that we're

FLORIDA PUBLIC SERVICE COMMISSION

10

1   asking -- basically one of our basic positions is we want a

2   separate calculation for high service pumping.

3             And we fully -- no change in position, but one last

4   element was we didn't take that extra step to show how you

5   calculate it.  And in this little change we say we're going to

6   do it exactly the same as we're suggesting for treatment.  That

7   is in my opinion a relatively minor clarification to more fully

8   explain how we recommend to you how to treat high service

9   pumping.  That's the only semi-substantive minor addition, no

10   change in position, to make it consistent with treatment.  The

11   other little change was a change of position which had no

12   substance.

13             Now as to everything else in the rule, all the other

14   little changes, additions and so forth, are absolutely and

15   completely supported by timely filed rebuttal testimony.  Now

16   --

17             CHAIRMAN CARTER:  That's a good place to break,

18   Mr. Reilly.

19             MR. REILLY:  Okay.

20             CHAIRMAN CARTER:  I'll give you one more second to

21   complete and wrap up.

22             MR. REILLY:  I would say only this --

23             CHAIRMAN CARTER:  Okay.

24             MR. REILLY:  -- that the proper time to have

25   perhaps -- we do this as a courtesy actually.  Instead of

FLORIDA PUBLIC SERVICE COMMISSION

11

1   tardy, it was two weeks before the hearing so everyone had it

2   to look at it.

3             Truthfully, I would suggest to the Commission as one

4   solution to this little problem is that we offer, just like

5   these other parties are offering modified exhibits to take into

6   account their rebuttal testimony, and we can do this either at

7   the time we put our witness on on direct; or even maybe more

8   appropriately when our witness is put on on rebuttal to say how

9   his testimony has changed, he'll say these changes I'm making

10   in my rebuttal testimony consequence changes in our revised

11   recommendation.  And really probably that's the most

12   appropriate time to, to take up the revised rule.

13             CHAIRMAN CARTER:  Thank you, Mr. Reilly.

14             Now, Mr. Hoffman, you're the only one --

15   Mr. Friedman, you're not to be heard on this; correct?  You're

16   not in this motion, are you?

17             MR. FRIEDMAN:  No, we didn't file a response.

18             CHAIRMAN CARTER:  Thank you.

19             MR. FRIEDMAN:  But we concur in Mr. Hoffman's

20   position.

21             CHAIRMAN CARTER:  Thank you.  Mr. Hoffman, you have

22   eight minutes.

23             MR. HOFFMAN:  Thank you, Mr. Chairman.  I'm going to

24   hand this one off to Ms. Rule.  As you heard from, from

25   Mr. Reilly, you know, it's kind of a mess.  You know, who can

FLORIDA PUBLIC SERVICE COMMISSION

12

1   follow really what he's talking about?  But I can tell you this

2   before I hand it off to Ms. Rule, the theme that we have, the

3   problem that we have is you've got, as Mr. Reilly said, stuff

4   that's in his rebuttal and stuff that wasn't anywhere.  Okay?

5   We have a right to file prefiled testimony responding to

6   assertions.  So if something was in his rebuttal or something

7   wasn't even there, we've never had that right.  So that's just

8   something to keep in mind.  Ms. Rule is going to go through the

9   various arguments that, that we have presented to the

10   Commission in our response.

11             CHAIRMAN CARTER:  Ms. Rule.

12             MS. RULE:  Thank you.  Actually Mr. Hoffman has

13   summarized them quite well.  You know, this is an evidentiary

14   hearing.  Public Counsel asked for an evidentiary hearing and

15   you granted it.  Along with that came a procedural order back

16   in September setting due dates for testimony and exhibits and

17   up until January 9th those dates have been followed.  And

18   that's less than two weeks before the hearing, and that's when

19   Public Counsel filed its motion seeking to revise its direct

20   testimony.  I mean, a revised exhibit to its direct testimony

21   is a revision of its direct testimony.

22             What I'm hearing today is, well, this is really part

23   of our rebuttal.  That's not what they've asked you to do.

24   They've asked you to permit them to revise their direct

25   testimony, and we object to a last-minute revision.  We'd ask

FLORIDA PUBLIC SERVICE COMMISSION

13

1   you to deny it for several reasons.  First, as we said in our

2   motion, Public Counsel -- I'm sorry, in our response, the

3   motion is late.  It's two weeks before hearing.  Public Counsel

4   really has offered you no reason in the motion or today why

5   this could not have been filed much earlier.

6             More importantly, however, this is an evidentiary

7   proceeding.  You have always required prefiled testimony and

8   exhibits in your evidentiary proceedings, and the purpose is

9   not only to give staff and the parties and the Commission an

10   opportunity to get prepared for hearing and a meaningful

11   opportunity to respond.

12             The problem here is permitting what is essentially a

13   change in direct testimony so late in the hearing process

14   deprives Aqua and other Intervenors of the right to conduct any

15   discovery.  We have to take Mr. Reilly's word here today what

16   has and hasn't changed.  We don't have the opportunity to

17   conduct discovery into what those changes mean.  This

18   introduces a great deal of uncertainty very late in the

19   process.  You know, even today, the day of the hearing,

20   Mr. Woodcock's testimony is not final until you rule on the

21   motion.  It's still a moving target for us.  Permitting a

22   change in testimony at this date certainly deprives Intervenors

23   of the right to respond by filing additional rebuttal testimony

24   and exhibits.  And this is important because, as you all know,

25   this is a very technical rule and Mr. Woodcock's testimony and

FLORIDA PUBLIC SERVICE COMMISSION

14

1   his revised exhibit propose technical changes.

2             And, finally, there's another reason why you should

3   not grant the motion.  Aqua will be prejudiced if the motion is

4   granted but Public Counsel will not be prejudiced if the motion

5   is not granted.  Posthearing briefs are due in this case on

6   February 19th, and at that point, of course, Public Counsel

7   will have the opportunity to make all of its recommendations to

8   you in whatever form it chooses.  It will not be harmed by

9   denial of its motion and we ask that you deny it.  Thank you.

10             CHAIRMAN CARTER:  Thank you very kindly.  We've heard

11   from both parties.  Now I'd like to hear from staff on the

12   preliminary matter --

13             MS. GERVASI:  Thank you, Mr. Chairman.

14             CHAIRMAN CARTER:  -- with your recommendation.

15             MS. GERVASI:  The staff has gone through the proposed

16   revised exhibit and we have determined that starting from

17   Line 13 on Page 6 of OPC's revised exhibit and going to the end

18   of Page 7 is indeed a new calculation that we have not seen and

19   is not in OPC's testimony, either direct or rebuttal testimony.

20   And although staff appreciates OPC's effort to update its

21   recommended rule language to incorporate areas of agreement

22   among the parties and staff, which is what they told us they

23   would like to do at the prehearing, we believe that it is

24   prejudicial to include new language, that coming in at this

25   late stage in the process precludes the other parties and staff

FLORIDA PUBLIC SERVICE COMMISSION

15

1   from doing any kind of discovery or from filing testimony in

2   response to it.  So our recommendation is to deny the motion

3   for that reason.

4             CHAIRMAN CARTER:  Okay.  Based upon the, both hearing

5   the parties and the recommendation from staff, we will deny the

6   motion.  And let's move with our further preliminary matters,

7   staff.

8             MS. GERVASI:  Thank you, Mr. Chairman.  There are

9   four proposed stipulations that the parties and staff have set

10   forth and they are --

11             CHAIRMAN CARTER:  This involves -- Commissioners,

12   excuse me for interrupting, this will involve all Commissioners

13   from this point further.  That was a preliminary matter that

14   was primarily with the Chair, but we are all on board now.  You

15   may proceed.

16             MS. GERVASI:  The four proposed stipulations appear

17   on Pages 20 and 21 of what has been marked as a Draft

18   Prehearing Order.  That Prehearing Order is in the process of

19   being filed in this form.  And we recommend that those four

20   proposed stipulations be approved.

21             CHAIRMAN CARTER:  Okay.  The -- are the parties, are

22   the parties in agreement with these proposed stipulations?  Any

23   party -- all parties are in agreement?  Mr. Reilly?

24   Mr. Hoffman?  Mr. Friedman?

25             MR. HOFFMAN:  Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

16

1             CHAIRMAN CARTER:  Commissioners, any questions or

2   comments on the proposed stipulations found on Pages 20

3   and 21 of the proposed Prehearing Order?  Commissioner Edgar.

4             COMMISSIONER EDGAR:  Mr. Chairman, if there is -- if

5   there are no questions, I'm prepared to make a motion in favor

6   of the proposed stipulations for Issues 1, 9, 12 and 13.

7             COMMISSIONER McMURRIAN:  Chairman.

8             CHAIRMAN CARTER:  You're recognized.  And seconded by

9   Commissioner McMurrian.

10             Commissioners, you've had a chance to hear the motion

11   and second, time to consider.  All in favor, let it be known by

12   the sound of aye.

13             (Unanimous affirmative vote.)

14             All those opposed.

15             Okay.  Staff, would you bring us back around to where

16   we should be now.

17             MS. GERVASI:  Thank you.  Yes, sir.  I wanted to

18   point out that all the parties have waived cross-examination of

19   two of the staff witnesses, so they have been excused from

20   appearing today.  That's witness Van Hoofnagle, who filed

21   testimony for staff, he's with the DEP, and also Witness Dwight

22   Jenkins with the St. Johns Water Management District has also

23   been excused.  The parties have waived cross-examination of

24   those two witnesses.

25             We have handed out what we've labeled a Comprehensive

FLORIDA PUBLIC SERVICE COMMISSION

17

1   Exhibit List for entry into the record which I would like to

2   have marked as Exhibit 1.

3             CHAIRMAN CARTER:  Show it done.

4             MS. GERVASI:  This exhibit shows all of the parties'

5   and staff's prefiled exhibits.  And the remaining exhibits, any

6   cross-examination exhibits will be offered into evidence as the

7   witness testifies, as well as the exhibits listed on the list

8   will be offered in at the, at the appropriate time.

9             CHAIRMAN CARTER:  Thank you.  Commissioners, we all

10   have the Comprehensive Exhibit List.  Show that marked as

11   Exhibit 1.

12             (Exhibit 1 marked for identification.)

13             MS. GERVASI:  Thank you.  That, I believe, brings us

14   to opening statements, which you allowed up to ten minutes per

15   side.

16             CHAIRMAN CARTER:  Okay.  Did we decide on who's going

17   first?  Mr. Reilly, I believe you're still --

18             MR. REILLY:  I think they set me up first and then

19   I've got three people coming right behind me.  If the first one

20   doesn't get me, then the next one will, I guess.

21             CHAIRMAN CARTER:  Well, I mean, you're an able

22   advocate.

23             MR. REILLY:  Well, I'll try.

24             CHAIRMAN CARTER:  And you have ten minutes, sir.

25   You're recognized.

FLORIDA PUBLIC SERVICE COMMISSION

18

1             MR. REILLY:  All right.  Thank you very much.  First,

2   the Citizens do appreciate the Commission's scheduling this

3   hearing and giving us an opportunity to present arguments and

4   testimony on how we believe this rule can be improved.

5             The Citizens recommend a methodology for calculating

6   used and useful for water treatment systems involving

7   separately evaluating the major components of water treatment,

8   which includes wells, storage and high service pumping.

9   Addressing each of these major components allows for a separate

10   accounting of the used and useful of each of the three major

11   components.  So if there is a significant difference between

12   the used and useful of each of the components, it can be

13   accounted for and adjusted accordingly.

14             The used and useful for each component is derived by

15   comparing a component's capacity to a component's demand.  The

16   used and useful percentage is essentially a fraction with the

17   demand numerator on the top with the capacity denominator on

18   the bottom of the fraction.  To the extent the demand is

19   greater and the capacity is less, the fraction is higher and

20   the used and useful percentage is higher.  To the extent the

21   demand is less and the capacity is greater, the fraction is

22   smaller and the used and useful is smaller.

23             Citizens believe it is important for the Commission's

24   new rule to fairly define and account for the demand that is

25   expected to be made in each of these three components by

FLORIDA PUBLIC SERVICE COMMISSION

19

1   current customers plus the statutory growth allowance, as well

2   as to fairly define and account for the capacity of each of

3   these three components that serve current customers in the

4   statutory growth.

5             The Citizens believe our recommendations concerning

6   the proposed rule will afford utilities the opportunity to

7   recover their prudent costs of providing sufficient quantity

8   and quality of water service to current customers and the

9   statutory growth allowance.

10             We all agree that water service is a vital,

11   life-sustaining commodity.  As Florida's population grows, the

12   availability, the affordability of this vital service is

13   increasingly becoming a statewide concern.  In light of this

14   issue of affordability it is very important that the

15   Commission's rule not require the overstating of the demand

16   numerator of the used and useful fraction and not require the

17   understating of the capacity denominator.

18             I'd like to briefly discuss just five subject areas

19   that we think are most important in this particular rule

20   proceeding.  First, one of the most important issues in this

21   docket is the proposed rules definition for firm reliable

22   capacity of water treatment system and storage.  While the

23   Citizens agree that the firm reliable capacity of a water

24   treatment system is equivalent to the pumping capacity of the

25   wells, excluding the largest well for those systems with more

FLORIDA PUBLIC SERVICE COMMISSION

20

1   than one well, we strongly disagree with expressing the

2   remaining capacity in gallons per day based only on 12 hours of

3   pumping.  Arbitrarily reducing by one-half all of the remaining

4   capacity unfairly limits the capacity denominator of the used

5   and useful fraction for water treatment systems with storage.

6   We do not believe this 12-hour limitation to be applied to all

7   regulated water systems throughout the entire State of Florida

8   is either based on sound engineering principles or valid

9   environmental requirements.

10             Our proposal is that the remaining pumping capacity

11   should be rated based upon 24 hours of pumping, unless there is

12   a documented restriction of hours of pumping as required by the

13   water management district or other regulatory body in which the

14   restriction shall apply.

15             Rather than establishing this arbitrary limitation on

16   the capacity denominator of the used and useful fraction, our

17   water treatment -- for water treatment systems with storage,

18   the Commission should defer to its sister agencies with respect

19   to water -- with the respective water management districts to

20   prescribe these types of well limitations.  After all, it is

21   the water management districts that have the expertise and the

22   specific information about each system, which is necessary to

23   establish well pumping limitations which are appropriate for

24   each and every specific water system.

25             The second matter which is very important to the

FLORIDA PUBLIC SERVICE COMMISSION

21

1   ratepayers is the proposed rule's multiple provisions provided

2   only to the utilities with opportunities to justify used and

3   useful, opportunities to justify used and useful calculations

4   which produce used and useful percentages that are higher than

5   what would be produced by the normal default provisions of the

6   rule.  These can be found -- there are seven such examples and

7   they're found in paragraphs (3), (4)(a), (b) and (c), (6),

8   (10) and (11).

9             The Citizens believe that there should be a single

10   paragraph that provides all parties, the utilities, OPC and

11   staff, with an equal opportunity to propose alternative

12   calculations when specific facts of the case warrant a

13   deviation from the normal default provisions of the rule.  Any

14   party, whether they be the utility, the Citizens or staff,

15   proposing an alternative calculation shall have the burden to

16   prove that the alternative calculation is more appropriate for

17   the specific case than the application of the normal default

18   calculation provided in the rule.

19             In several instances -- OPC has recommended in some

20   cases, and even staff and the utilities have agreed, that some

21   of the provisions in the proposed rule should be relocated to

22   this alternative calculation provision and we believe that's

23   really where it belongs.

24             Thirdly, Paragraphs (4)(a), (b) and (c) provide for

25   circumstances where a water treatment system shall be

FLORIDA PUBLIC SERVICE COMMISSION

22

1   considered 100 percent used and useful.  The Citizens strongly

2   disagree that these circumstances should automatically cause a

3   treatment system to be considered 100 percent used and useful.

4   With the exception that a system that is built out and there is

5   no potential for expansion of the service territory and it's

6   prudently designed, then a system may be considered 100 percent

7   used and useful.

8             Fourth, Paragraph (1)(d) defines peak demand for

9   storage.  The Citizens agree with the definitions provision to

10   exclude excessive unaccounted for water, its provision for

11   growth allowance and its fire flow provision, but we do

12   disagree basing peak demand for storage on maximum day flow

13   rather than 25 percent of maximum day flow.  We believe the

14   latter provision is more appropriate and more fair to the

15   customers.

16             And, finally, the Citizens believe that the rule

17   should provide a separate used and useful calculation for high

18   service pumping, the rule should include a definition for high

19   service pumping, for peak demand for high service pumping, for

20   firm reliable capacity for high service pumping and a separate

21   used and useful calculation for used and useful pumping -- for

22   high service pumping.  These are Issues basically 16 through 20

23   in your Prehearing Order.

24             A separate used and useful calculation of high

25   service pumping will not necessarily increase or decrease a

FLORIDA PUBLIC SERVICE COMMISSION

23

1   system's rate base, revenue requirement or resulting rates.  It

2   will depend entirely upon the specific facts of the case, the

3   capacity of the pumps and the demand which is being placed on

4   them.  Separate analysis of high service pumping will cause

5   either lower rates in some cases and higher rates in others.

6   But, nevertheless, we propose a separate calculation because

7   high service pumping is a separate and distinct component from

8   both treatment and storage.  The calculation of storage has

9   nothing to do with high service pumping.  Evaluating high

10   service pumps separate from storage is necessary to provide an

11   accurate calculation of used and useful and it can be done

12   relatively easily.

13             Again, thank you for this opportunity.  Those are our

14   most important points and that concludes our opening remarks.

15             CHAIRMAN CARTER:  Thank you, sir.  If you feel

16   compelled, you still have two minutes to go.

17             MR. REILLY:  I'll reserve that time.

18             CHAIRMAN CARTER:  All right.  I believe Mr. Hoffman

19   or Friedman, who's on second?  Who drew the short straw?

20             MR. REILLY:  I was going to say --

21             MR. FRIEDMAN:  Mine is probably going to be brief,

22   the briefest.

23             CHAIRMAN CARTER:  Wait one second.  Mr. Reilly.

24             MR. REILLY:  -- I used the extra two minutes on the

25   other argument.  See, it all evens out.

FLORIDA PUBLIC SERVICE COMMISSION

24

1             CHAIRMAN CARTER:  Good deal.  Mr. Friedman.

2             MR. FRIEDMAN:  Thank you, Mr. Chairman,

3   Commissioners.

4             I believe that the intent was to adopt a rule that

5   had the broadest applicability and thus would reduce rate case

6   expense while providing the flexibility to address unique

7   situations.  We believe that the proposed rule accomplishes

8   that task.  Although all of Utility, Inc.'s positions are not

9   incorporated in the proposed rule, Utilities, Inc. believes

10   that it is a reasonable compromise.  While we would always like

11   to have everything our way, as would, I'm sure, each of you,

12   that's not generally reality.  And thus Utilities, Inc. accepts

13   the proposed rule with the changes that everybody has

14   stipulated to as a reasonable compromise between the interests

15   of the citizens and the customers of these utilities and the

16   regulated industry, and we would ask that the rule as proposed

17   be adopted without changes to complicate it further.  Thank

18   you.

19             CHAIRMAN CARTER:  Okay.  One second, Mr. Hoffman.

20             Mr. Hoffman, you're recognized.

21             MR. HOFFMAN:  Thank you, Mr. Chairman.  I'm going to

22   ask Ms. Rule to distribute just another copy of the proposed

23   rule that was approved by the Commission prior to the Public

24   Counsel's request for hearing.  You have that.  I think in your

25   notebooks it's an exhibit to Mr. Redemann's testimony.  But

FLORIDA PUBLIC SERVICE COMMISSION

25

1   just in case you want to pull it up real quick, that's all that

2   is.  It's just another copy of that proposed rule.

3             Mr. Chairman, let me begin by stating that Aqua

4   applauds the efforts of the staff over the course of the last

5   two years to essentially corral the affected parties and the

6   numerous positions and the numerous proposed rule language

7   alternatives and develop them into a proposed rule which we

8   think for the most part does an excellent job of balancing the

9   competing positions of the parties and developing methodologies

10   and principles, which, if adopted, we think will reduce the

11   amount of litigation on used and useful issues.  And that is

12   really to the ultimate benefit of our customers who pay for

13   these costs of litigation through rate case expense.

14             I should also say that the proposed rule for the most

15   part codifies and reflects prior Commission orders and rulings,

16   which I think gives a level of consistency to the Commission's

17   approach in connection with this particular issue.

18             Now having expressed my client's admiration for the

19   proposed rule, you know, once the Office of Public Counsel

20   launched sort of a wholesale assault on the rule, we viewed

21   this as an opportunity to come before you and offer the expert

22   testimony of one of the renowned experts in the field, and

23   that's Mr. Guastella, to respond to the Public Counsel's

24   suggestions and to give you a limited set of suggested

25   alternatives to the Commission's proposed rule.  And what I'd

FLORIDA PUBLIC SERVICE COMMISSION

26

1   like to do is just run very briefly through those, through

2   Aqua's alternative proposals.

3             And the first is in connection with Subsection

4   (1)(a).  We happen to agree with the Office of Public Counsel

5   that high service pumps should be separated from storage

6   facilities for the purpose of identifying their cost and

7   percentage used and useful.  Where we disagree with the Office

8   of Public Counsel is we believe that the used and useful

9   calculation for high service pumps cannot be reduced to a

10   simple formula and, therefore, we don't think there's a need

11   for a separate rule provision on this particular issue.

12             The staff witness, Mr. Redemann, has testified, will

13   be testifying in this case that in most cases we're talking

14   about a relatively small level of investment in connection with

15   the entire water treatment system when you're talking about the

16   high service pumps.  And as Mr. Guastella will testify, there

17   are often times very system-specific factors such as the

18   configuration of the pipes, the specific operation of more than

19   one high service pump that really make it impractical and

20   inappropriate to try to put used and useful for high service

21   pumps into sort of, some sort of snapshot formula.

22             Secondly, we agree in part with the staff and parties

23   with the way in which the inclusion of fire flow is laid out in

24   the proposed rule.  You can find that in Sections (1)(c) and

25   (1)(d).  But we're suggesting that additional language is

FLORIDA PUBLIC SERVICE COMMISSION

27

1   appropriate here to allow recovery for what we call an

2   appropriate amount of fire flow.  Why?  To ensure that

3   utilities can recover the cost of fire flow requirements from

4   multiple hydrants throughout an entire service area.  We think

5   it's critical in today's times that utilities recover the cost

6   of ensuring adequate fire flow throughout the entire service

7   area, throughout the entire system to combat incidents of

8   multiple fires and coincidental fires.  Got to have that.

9             Third, we disagree with the staff proposed rule to

10   the extent it proposes to reduce peak demands by excessive

11   unaccounted for water.  Mr. Guastella supports the proposition

12   that the cost of water treatment facilities does not go down if

13   the system's lost and unaccounted for water becomes excessive

14   over time.  The costs to the facilities do not go down.

15             Aqua believes that any adjustments for excessive

16   unaccounted for water should be limited to operating expenses.

17   When it comes to plant, when it comes to water treatment

18   facilities, the more appropriate response, we believe, is to

19   order the utility to undertake a cost-benefit analysis to

20   determine if the cause of the excessive unaccounted for water

21   should be repaired, and, if so, they should fix it.

22             Fourth, we propose that peak demands, whether they're

23   expressed as maximum day or peak hour, should not be limited to

24   a rate setting test year because a rate setting test year has

25   no relationship to the real world engineering design of a water

FLORIDA PUBLIC SERVICE COMMISSION

28

1   treatment system.  These systems are not designed by engineers

2   for a rate setting test year.  Instead, they're designed for

3   the maximum demand, whether that occurs last year, the year

4   before, the year before that or during the test year.

5             Finally, we disagree with the provisions in the rule

6   which basically say that if there's an unusual occurrence on a

7   single max day or peak hour when you're determining peak

8   demand, that the utility should then move to the average of the

9   five highest days.  We believe that consistency would have you

10   change this provision so that if there's an unusual occurrence

11   on the single max day, then the rule should say that the

12   utility would simply go to the next highest maximum day, so

13   long as there's not an unusual occurrence on the next highest

14   maximum day.

15             Those are our proposals.  I appreciate your time, and

16   that concludes our opening remarks.

17             CHAIRMAN CARTER:  Thank you very much.

18             Let me finish my note here.  I believe that we've

19   completed our preliminary matters.  We've had opening

20   statements of the parties, and we're now ready to swear in

21   witnesses; correct?

22             MS. GERVASI:  Yes, sir.  One thing.

23             CHAIRMAN CARTER:  Yes, ma'am.

24             MS. GERVASI:  I meant, I meant to offer in Exhibit 1

25   into evidence earlier and would like to offer that in at this

FLORIDA PUBLIC SERVICE COMMISSION

29

1   time.  I don't believe there's any objection to that.

2             CHAIRMAN CARTER:  No objections?  No objections.

3   Show it done.

4             MS. GERVASI:  Thank you.

5             MR. REILLY:  Which exhibit?

6             MS. GERVASI:  Exhibit 1.

7             CHAIRMAN CARTER:  Exhibit 1, the Comprehensive

8   Exhibit List.

9             MR. REILLY:  Okay.  All right.  Thanks.  Okay.

10             MS. GERVASI:  Thank you.

11             (Exhibit 1 admitted into evidence.)

12             CHAIRMAN CARTER:  Okay.  Any other preliminary

13   matters?

14             MS. GERVASI:  No, sir.

15             CHAIRMAN CARTER:  Any preliminary matters of any of

16   the parties?

17             Okay.  Are all the witnesses here?  I would ask all

18   the witnesses, would you stand and be sworn in, please.  And

19   raise your right hand.

20             MS. GERVASI:  There's one other witness, I believe.

21   Thank you.

22             CHAIRMAN CARTER:  Do we have all witnesses?  Calling

23   all witnesses.

24             (Witnesses collectively sworn.)

25             Okay.  You may be seated.

FLORIDA PUBLIC SERVICE COMMISSION

30

1             Okay.  Mr. Reilly, you are recognized.

2             MR. REILLY:  Yes.  We'd like to offer Mr. Woodcock to

3   the stand.

4             CHAIRMAN CARTER:  Mr. Woodcock.

5             MR. REILLY:  Would you -- are we ready?

6             CHAIRMAN CARTER:  You're ready.

7                         ANDREW T. WOODCOCK

8   was called as a witness on behalf of the Citizens of the State

9   of Florida and, having been duly sworn, testified as follows:

10                         DIRECT EXAMINATION

11   BY MR. REILLY:

12        Q    Okay.  Would you please state your name and business

13   address for the record.

14        A    My name is Andy Woodcock.

15             CHAIRMAN CARTER:  One second.  We can't hear you.

16   Could you pull the microphone a little closer or just move --

17             THE WITNESS:  Is this better?

18             CHAIRMAN CARTER:  That's much better.

19             THE WITNESS:  Okay.  My name is Andy Woodcock.  My

20   business address is 201 East Pine Street, Suite 1000, Orlando,

21   Florida 32801.

22   BY MR. REILLY:

23        Q    All right.  Mr. Woodcock, did you prefile direct

24   testimony including attached exhibits in this docket?

25        A    I did.

FLORIDA PUBLIC SERVICE COMMISSION

31

1        Q    If I were to ask you the same questions posed in your

2   prefiled direct testimony, would your answers be the same as

3   outlined in your prefiled direct testimony filed on November 5,

4   2007?

5        A    They would be.

6        Q    Excuse me?

7        A    They would be.

8        Q    Well --

9        A    I'm sorry.  We're talking about exhibits also.  I

10   apologize.

11        Q    No.  Actual testimony too, because I believe you

12   filed rebuttal testimony.

13        A    Yes.  I have filed rebuttal testimony in this case,

14   and it would be revised accordingly.

15        Q    Repeat that again now.  I guess my question is if I

16   asked you the same questions I posed to you in your prefiled

17   direct, would your answers be the same as you, as you made in

18   your direct testimony?

19        A    No, they would not.

20        Q    And in what way would they be different?

21        A    They would be different to the extent that my

22   rebuttal testimony that's been filed in this alters my direct

23   testimony.

24        Q    Okay.  That is as to your testimony.

25        A    Correct.

FLORIDA PUBLIC SERVICE COMMISSION

32

1        Q    And do you continue to endorse and support the

2   exhibits in your prefiled direct testimony?

3        A    With respect to Exhibit 2, there are several

4   revisions that occurred due to changes in my rebuttal

5   testimony.  And there is also an additional change in Exhibit 2

6   to clarify the peak demands for high service pumping.

7             MR. HOFFMAN:  I'm going to object and move to strike,

8   Mr. Chairman.  We've already heard on this.  I'm surprised that

9   Public Counsel is presenting this.  You just ruled this morning

10   that that proposed revised Exhibit 2 to his direct testimony

11   would not be permitted into the record of this proceeding.  So

12   I would move to strike that last statement.  And I would, I

13   would further move that for the remainder of this proceeding

14   that the witness be precluded from testifying to the new

15   material in his proposed revised Exhibit 2 to his direct

16   testimony.

17             MR. REILLY:  With all due respect, I believe the

18   Commission should afford the Citizens an opportunity to explain

19   what is in the revised exhibit and that it is, in fact,

20   supported completely by the -- but the appropriate time is at

21   the rebuttal testimony.  I'm not sure what the wish of the

22   Commission is, but, but --

23             CHAIRMAN CARTER:  The ruling stands.  I'm going to

24   have to sustain the objection.  The ruling stands, Mr. Reilly.

25

FLORIDA PUBLIC SERVICE COMMISSION

33

1   BY MR. REILLY:

2        Q    Okay.  So your answer is you do not support your

3   exhibit as, as stated except to the extent that your rebuttal

4   testimony --

5        A    Correct.

6        Q    Okay.  All right.  With the modifications that you

7   have described --

8             CHAIRMAN CARTER:  I believe -- thank you,

9   Mr. Hoffman.

10             MR. HOFFMAN:  Yes.

11             CHAIRMAN CARTER:  I believe we want to not refer from

12   any of the information pursuant to our initial ruling, so just

13   conduct yourself in that manner.

14             MR. REILLY:  Okay.  Then I would say at this time I

15   would move Mr. Woodcock's prefiled direct testimony be inserted

16   into the record as though read with the qualifications that he

17   made as to the fact that his prefiled direct testimony is

18   obviously modified by his properly filed rebuttal testimony.

19             MR. HOFFMAN:  I'm going to object to that, Mr.

20   Chairman, with all due respect.  This is getting muddled again.

21   You've already made a ruling with respect to the proposed

22   revised Exhibit 2 to Mr. Woodcock's prefiled direct testimony.

23   Now it was the Public Counsel who wanted to separate rebuttal

24   from direct testimony in this proceeding.  Now it looks as

25   though they're trying to cure the problems with their revised

FLORIDA PUBLIC SERVICE COMMISSION

34

1   exhibit, with their Exhibit 2 by incorporating the rebuttal

2   testimony so they can make arguments later in their posthearing

3   brief, and I've got a real objection to this.  I think that the

4   proper procedure, Mr. Chairman, with all due respect, is for

5   this witness to address his direct testimony and his exhibits

6   as filed and not attempt at this late juncture to make changes

7   to those by sort of vaguely incorporating things that are in

8   his rebuttal testimony.

9             MR. REILLY:  May I respond?

10             CHAIRMAN CARTER:  You're recognized, Mr. Reilly.

11             MR. REILLY:  As to this exhibit, I'm not going to be

12   offering or sponsoring the AT-2 attached to the direct

13   testimony because it has changed materially.  I'm not that

14   concerned about that.  All I'm going to be moving in is his

15   testimony as filed but as qualified by his properly filed

16   rebuttal testimony.

17             Our pre, our prefiled procedure approved in this

18   order is that Public Counsel shall file direct testimony, that

19   the other parties will file their direct testimony responding

20   to that.  And Public Counsel was offered -- in our procedure

21   was allowed to file rebuttal testimony that took into account

22   the testimony filed by the utilities and staff.  That is

23   exactly what we have done.  So at the proper time we will be

24   identifying and moving in our rebuttal testimony which was

25   filed exactly when it should have been.

FLORIDA PUBLIC SERVICE COMMISSION

35

1             So I am abandoning the ATW-1 and 2, but I believe

2   it's absolutely proper for me to file, to, to offer into

3   testimony this direct testimony as modified by the rebuttal

4   testimony that is, that we will be taking up at later time.

5   Now we don't have to -- we can -- I think we're going to be

6   addressing the rebuttal testimony and questions about the

7   rebuttal testimony at a later time.  But it's important to

8   accept the direct testimony with the understanding that later,

9   properly filed, timely filed rebuttal testimony has been filed

10   in this docket with full notice and everything to everybody.

11   There's no -- that's absolutely consistent with our procedure.

12             So in light of your ruling, I am, I am not going to

13   worry about moving into the record the exhibit.  It was really

14   offered as a convenience to the parties.  We can make our

15   points with our testimony, we can make our points with our

16   rebuttal testimony, all timely, properly filed.

17             So I have -- in light of this ruling, I'm not going

18   to worry about moving into the record the exhibit.  But we have

19   two sets of testimony properly filed and at the proper time --

20   and we have every right to move that and to make it available

21   for people to cross-examine.  So what we are doing right now is

22   we're moving in his prefiled direct testimony, which he still

23   endorses in all respects except to the extent that it has been

24   modified by the rebuttal testimony which was timely and

25   properly filed.  That is our, what we're asking to be moved

FLORIDA PUBLIC SERVICE COMMISSION

36

1   into the record.

2             CHAIRMAN CARTER:  Mr. Hoffman, and then I'm going to,

3   then I'm going to look to staff.

4             MR. HOFFMAN:  Very briefly, Mr. Chairman.  This sort

5   of underscores the concern that we had when we opposed their

6   motion.

7             Mr. Reilly doesn't need to file that revised exhibit

8   to a large degree now if he's allowed to basically change his

9   direct testimony by incorporating his rebuttal testimony.  If

10   you recall, one of the, one of the main concerns and objections

11   that we had to what Public Counsel was doing was that by

12   revising their direct we did not have our opportunity to

13   address that in prefiled rebuttal.  So this to me, with all due

14   respect, is sort of an end around to your ruling.  They will

15   have the opportunity, they have it right now, to put in their

16   direct testimony.  And then -- and they wanted to keep it

17   separate.  They'll have the opportunity to separately put in

18   their rebuttal testimony.

19             CHAIRMAN CARTER:  Staff.

20             MS. GERVASI:  Staff agrees with that.  The witness is

21   on the stand now to take cross-examination based on his direct

22   testimony.  To the extent that his rebuttal testimony modifies

23   his direct testimony, he will have an opportunity on

24   cross-examination on rebuttal.  The testimonies will speak for

25   themselves.

FLORIDA PUBLIC SERVICE COMMISSION

37

1             CHAIRMAN CARTER:  So the bottom line?

2             MS. GERVASI:  Is that -- I don't know if there's a

3   motion on the table -- that his direct testimony should be

4   offered in as though read and then later his rebuttal should be

5   offered in as though read at the appropriate time.

6             CHAIRMAN CARTER:  Okay.

7             MR. REILLY:  And that's fine with Public Counsel.  I

8   mean, just so the Commission understands we're -- there are two

9   sets of testimony.  One is later in time.  So we'll move in --

10   I'm asking to move in this direct testimony at this time.  To

11   the extent he gets cross-examination questions that probes his

12   actual language of that direct testimony that's different, then

13   I assume he'll clarify that at the time.  So we basically move

14   the direct testimony at this time.  And when we approach the

15   rebuttal, we'll do the same at that time.

16             CHAIRMAN CARTER:  So the testimony of the witness,

17   the direct testimony of the witness pursuant to the ruling

18   shall be entered into the record as though read.

19             MR. REILLY:  And that's right.  And to clarify, we

20   are moving in or asking to identify for cross-examination

21   purposes ATW-1, which is just merely his qualifications.  We

22   will not bother to identify and move into the record

23   ATW-2 because, for the reasons you already know.

24             MS. GERVASI:  And just for clarification of the

25   record, ATW-1 has been marked as Exhibit 2 on the Comprehensive

FLORIDA PUBLIC SERVICE COMMISSION

38

1   Exhibit List.  ATW-2 has been marked as Exhibit 3.

2             (Exhibit 2 marked for identification.)

3             CHAIRMAN CARTER:  Okay.  We'll do -- we'll take care

4   of the exhibit as we normally do at the end of the testimony.

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

65

1             CHAIRMAN CARTER:  Mr. Reilly, you are recognized.

2             MR. REILLY:  Okay.  I guess I would ask Mr. Woodcock

3   to provide a brief five-minute summary.

4             THE WITNESS:  Thank you.

5             CHAIRMAN CARTER:  Mr. Woodcock.

6             THE WITNESS:  I am of the opinion that the proposed

7   rule set forth should set forth the general methodology and

8   guidelines for calculating used and useful for water systems;

9   however, there may be special cases where deviations from the

10   guidelines may be required.  Therefore, it is important that

11   the rule contain a provision to allow any party the ability to

12   present alternative methodologies to calculating used and

13   useful should the specific facts of a case require.  I

14   recommend several changes to the proposed rule; however, in my

15   summary I will touch on the major issues.

16             The proposed rule would have the firm capacity for

17   water treatment systems with storage be based upon wells

18   operating for 12 hours instead of 24.  This provision

19   essentially doubles the used and useful of a water treatment

20   system.  The maximum capacity a well can produce in a day is

21   equivalent to the water it will produce in 24 hours, and

22   prudent and efficient design would seek to maximize that

23   pumping time.  There may be circumstances where the capacities

24   of wells may be limited due to aquifer characteristics or salt

25   water intrusion; however, the solutions to these issues are

FLORIDA PUBLIC SERVICE COMMISSION

66

1   never as simple as reducing pumping times to 12 hours.  I

2   believe a more accurate used and useful percentage can be

3   obtained by allowing for a provision for pumping less than 24

4   hours should it be required or mandated by the water management

5   district or other regulatory agency.

6             I am of the opinion that the provision for

7   alternative calculations in proposed Paragraph 3 of the rule

8   should be expanded to allow all parties, the utility, staff and

9   Intervenors, the ability to deviate from the prescribed

10   methodology of the rule where circumstances warrant it.  In

11   these cases I believe each party should have the burden of

12   proof in documenting their position.  I also believe that there

13   are many cases throughout the proposed rule that can be

14   incorporated in this paragraph, including economies of scale,

15   service area restrictions, limiting factors involving treatment

16   capacity, well drawdown limitations and changes in flow due to

17   conservation or a reduction in number of customers.

18             There are certain provisions in Paragraph 4 of the

19   proposed rule that would automatically allow a water treatment

20   system to be 100 percent used and useful.  The provision for

21   allowing a single well system to be automatically considered

22   100 percent used and useful does not account for the fact that

23   that well may only be actually partially utilized by the

24   customers.

25             Another provision of Paragraph 4 would allow for

FLORIDA PUBLIC SERVICE COMMISSION

67

1   100 percent used and useful for systems that are built out with

2   no room for expansion.  I am of the opinion that this

3   represents a special case that could handled under the

4   alternative methodology paragraph.

5             Additionally, I find the proposed peak demand for

6   storage to be equivalent to the maximum day demand to be

7   excessive and recommend that the FDEP requirement of 25 percent

8   of the maximum day demand be used to more accurately reflect

9   design requirements.  Under the proposed rule, a storage tank

10   that is appropriately designed for 25 percent of maximum day

11   per the DEP criteria would automatically be considered

12   100 percent used and useful if it were actually only serving

13   customers to an extent of 50 percent of its capacity.

14             As currently proposed, the high service or the -- as

15   currently proposed, the rule does not account for the separate

16   calculation of high service pumps.  I am of the opinion that

17   high service pumps are a separate and distinct component from

18   both storage and treatment and play a fundamental role in

19   providing service to customers.  My separate evaluation of high

20   service pumps is not burdensome, nor does it overly complicate

21   the rule.  My recommendation is to provide a separate used and

22   useful calculation for high service pumps in order to provide

23   for more accuracy.  And that's my summary.

24             MR. REILLY:  Okay.  We would tender Mr. Woodcock for

25   cross-examination.

FLORIDA PUBLIC SERVICE COMMISSION

68

1             CHAIRMAN CARTER:  Okay.  Mr. Hoffman, you're

2   recognized.

3             MR. HOFFMAN:  Thank you, Mr. Chairman.

4                          CROSS EXAMINATION

5   BY MR. HOFFMAN:

6        Q    Good morning, Mr. Woodcock.

7        A    Good morning.

8        Q    My name is Ken Hoffman.  I represent Aqua Utilities

9   Florida.

10             Have you ever previously testified before this

11   Commission on the issue of used and useful plant in service?

12        A    Not before the Florida Public Service Commission.

13        Q    Let me ask you to turn to, let me ask you to turn to

14   your Exhibit ATW-1, which is your resume.  And take a look at

15   Pages 2 and 3 of that document, if you would.

16             Would you agree that all of your work for the

17   11 listed clients, with the exception of the Office of Public

18   Counsel, has been on behalf of governmental utility entities?

19        A    Yes.

20        Q    Would you agree that governmental authorities such as

21   a county water utility or a municipal water utility do not

22   establish rates based on used and useful calculations?

23        A    That is correct.

24        Q    Do you agree that the, that this Commission must

25   allow a utility the opportunity to recover the full cost of

FLORIDA PUBLIC SERVICE COMMISSION

69

1   serving existing customers on a current basis as well as for a

2   reasonable future period after meeting the demands of customer

3   growth?

4        A    Could you restate that again?  I'm sorry.

5        Q    Yes, sir.  Do you agree that this Commission must

6   allow a utility the opportunity to recover the full cost of

7   serving existing customers on a current basis as well as for a

8   reasonable future period after meeting the demands of customer

9   growth?

10        A    To the extent that that is part of the regulatory

11   process, yes.

12        Q    Do you agree that water systems are designed on the

13   basis of meeting estimated maximum demands for design purposes

14   that are typically greater than customers will ultimately

15   impose?

16        A    In some cases, yes, but not in all.

17        Q    And would you agree that typically safety factors or

18   cushions are built into the design maximum demands?

19        A    Yes.

20        Q    Would you agree that the Commission's proposed rule

21   which is at issue in this hearing reflects the use of actual

22   maximum demands, not the higher demands used for design

23   purposes?

24        A    It is based on the actual demands that the customers

25   utilize in a system.

FLORIDA PUBLIC SERVICE COMMISSION

70

1        Q    So that would be a yes to my question?

2        A    Yes.

3        Q    Can we then agree that the proposed rules are

4   conservative from the standpoint that they incorporate actual

5   demand, actual maximum demands as opposed to the higher demands

6   that are used for design purposes?

7        A    I'm sorry.  Can you repeat that again?

8        Q    Yes.  You answered yes to my question that the

9   proposed rule reflects actual maximum demands, not the higher

10   demands for design purposes; correct?

11        A    Correct.

12        Q    And with that would you agree then that the proposed

13   rules are conservative?

14        A    No, I do not.

15        Q    Okay.  You do agree that the, that the number that is

16   used in the proposed rule for demands is lower.  In other

17   words, actual maximum demands are lower than the higher demands

18   used for design purposes.

19        A    In some cases it may be, yes.

20        Q    Do you agree with Mr. Guastella that one objective of

21   the proposed rule is to establish reasonable used and useful

22   criteria that eliminate unnecessary and costly controversy?

23        A    To the extent that that can be embodied with the

24   flexibility provisions of the rule, yes.

25        Q    Do you agree with Mr. Redemann's statement in his

FLORIDA PUBLIC SERVICE COMMISSION

71

1   testimony that used and useful litigation results in

2   substantial rate case expense which is ultimately passed on to

3   the ratepayers?

4        A    I cannot really speak to the magnitude of used and

5   useful rate case expense versus other rate case expenses.

6        Q    Okay.  All right.  Let me ask that again because I

7   didn't ask you about the magnitude.  Do you agree with

8   Mr. Redemann's statement that used and useful litigation

9   results in substantial rate case expense -- actually I did ask

10   you about the magnitude.  I'm sorry.

11             Do you understand that the costs of used and useful

12   litigation are passed on to a utility's customers?

13        A    That is my understanding.

14        Q    Okay.  Do you think that the general purpose of an

15   agency's rulemaking process should be to codify an agency's

16   policies to avoid repeated litigation over the same issue?

17        A    Can you repeat that one again?

18        Q    Sure.  Do you believe that the general purpose of an

19   agency's rulemaking process should be to codify an agency's

20   policies through, that have been developed through litigation

21   so as to avoid future repeated litigation over the same issue?

22        A    I guess I would have to conditionally agree to that

23   to the extent that I'm not involved very frequently in

24   rulemaking as a procedure.

25        Q    Okay.  Wouldn't you hope that one of the goals of

FLORIDA PUBLIC SERVICE COMMISSION

72

1   this whole rulemaking process is to have the Commission issue a

2   rule that, for example, on a particular issue that's been

3   litigated 12 times, that the Commission would now have a rule

4   and thereby eliminate continued litigation on that particular

5   issue?

6        A    Yes, I would.

7        Q    Would you agree that the more expressly stated and

8   defined rules and methodologies that the Commission

9   incorporates into this rule, the less litigation that there

10   will be in the future over specific used and useful issues?

11        A    I would agree.  But there's an important point to

12   make here, especially with respect to used and useful in water

13   utilities.  It's one thing to codify rules to make things

14   administratively expedient, but those rules also have to be

15   carefully considered in the fact that they're not glossing over

16   or causing potential inequities that could better be handled by

17   some flexibility in those rules.

18        Q    Okay.  Let me, let me ask you a few questions about

19   that particular issue, flexibility, which you just mentioned in

20   your last response.

21             Would you accept, subject to check, that in your

22   prefiled direct testimony you have made five separate

23   recommendations where you recommend that a provision of the

24   proposed rule be removed and covered under this alternative

25   methodology section?

FLORIDA PUBLIC SERVICE COMMISSION

73

1        A    Subject to check of the number five, yes.

2        Q    Isn't it your position that an alternative

3   calculation provision in the rule should capture only special

4   or unique cases?

5        A    Yes.

6        Q    Is it your position that a determination of prudence

7   of investment is something special or unique?

8        A    No.  It's something that's fundamental to the entire

9   rate process is my understanding.

10        Q    Wouldn't you agree that consideration of economies of

11   scale is not special or unique?

12        A    I think that it is special and unique to the extent

13   that economies of scale can be addressed in used and useful

14   many different ways, and it's difficult to specifically codify

15   how one would handle economies of scale.

16        Q    But the truth is -- in your experience isn't the

17   issue and the consideration of economies of scale something

18   that is typically done in the design and engineering of water

19   treatment plant?

20        A    It is occasionally considered, yes.

21        Q    Would you agree that a situation where a water system

22   is built out with no further opportunity for expansion is not

23   unique in the State of Florida?

24        A    You know, I can't really speak on my experience if

25   that's the case or not.  I would not say that -- I don't know.

FLORIDA PUBLIC SERVICE COMMISSION

74

1   As a general rule I could not tell you that.

2        Q    You don't know one way or the other?

3        A    Right.

4        Q    Would you agree that there is nothing special or

5   unique about the pumping capacity of a water treatment system

6   being limited by something, by something such as the treatment

7   capacity or drawdown limitations?

8        A    It can be a special case.  It certainly is a unique

9   case when you're trying to codify these rules on a set of

10   standards.  Such things that can change, what type of the

11   treatment process is limiting, what are the well drawdown

12   calculations, all of those are different from system to system.

13   The concept may be in many systems or some systems, but the

14   specific addressing of those issues is different for every

15   system.

16        Q    So the concept is not, is not unique, but the

17   numbers, the specific application to a system certainly changes

18   from system to system.  Is that a fair statement?

19        A    The method of calculation could certainly change from

20   system to system.

21        Q    Is it unusual or unique to see a decrease in flows

22   due to conservation or a reduction in the number of customers?

23        A    No.  You take away demand, you're going to see less

24   demand.

25        Q    Now --

FLORIDA PUBLIC SERVICE COMMISSION

75

1        A    But to the extent that, once again, from system to

2   system the magnitude or the degree or the causes of reductions

3   in flows, once again, very different from system to system.

4        Q    Let me, let me ask you a few questions about this

5   issue of high service pumps that you talk about on Pages 7

6   and 8 of your testimony.  Isn't it true that many small water

7   systems do not have high service pumps?

8        A    In many small water systems without ground storage

9   the well pumps actually act as high service pumps.

10        Q    Was that a yes or a no?

11        A    I would say all systems have high service pumps,

12   small or big.

13        Q    Okay.  But in small systems I think your answer is

14   other pumps that are not high service pumps serve a high

15   service pumping capacity.  Isn't that what you're saying?

16        A    High service pumping is a function, it's not just a

17   label you tag on a pump.  The definition of high service

18   pumping is essentially the last pump that provides service to

19   the customers.

20             Now in the case of small systems or even maybe medium

21   size systems you will have a system where the only pump in the

22   water treatment system is the well pump.  To the extent that

23   it's providing the high service directly to the customers, that

24   is considered a high service pump.  It is also the well pump.

25        Q    You studied and filed testimony in Aqua's last rate

FLORIDA PUBLIC SERVICE COMMISSION

76

1   case, did you not?

2        A    Yes.

3        Q    Okay.  Isn't it true that, subject to check, that in

4   that rate filing which contained 56 water systems that Aqua

5   only had, that Aqua had high service pumps for only 14 out of

6   56 of those systems?

7        A    Subject to check.  I really don't --

8        Q    You would agree with that?

9        A    I really don't know the number.  There were some that

10   did and some that didn't.

11        Q    Okay.  Would you accept, subject to check, that only

12   14 out of 56 water systems had high service pumping facilities?

13        A    No.  They all had high service pumping facilities of

14   some sort.  Like I said before, they may have been the well

15   pumps providing that high service function.  So I would say all

16   54 did.

17        Q    Okay.  Would you accept, subject to check, that only

18   14 out of 56 water systems in that case had high service pumps?

19        A    Once again, high service pumps -- the well pumps

20   could be high service pumps, and I believe every, every system

21   in that case had wells.

22        Q    Did you calculate a used and useful percentage for

23   high service pumps for all 56 of those water treatment systems?

24        A    I did.

25        Q    Would you agree that for water systems that have

FLORIDA PUBLIC SERVICE COMMISSION

77

1   multiple high service pumps that the capacity of those pumps

2   alone is not sufficient to show their used and useful

3   percentage?

4        A    I disagree with that.

5        Q    Would you agree that, that typically high service

6   pumps connect to a common transmission main?

7        A    Yes.

8        Q    Would you agree that when two or more high service

9   pumps are operated at the same time that they pump against

10   pressure resulting in flow rates that are less than their rated

11   capacity?

12        A    Not necessarily.  When you're doing proper design of

13   high service pumping facilities, you know how many high service

14   pumps you're going to put together.  You're going to rate the

15   capacity of each of those pumps knowing that they're actually

16   going to be operating within an envelope of operation ranges.

17   Generally in design the rated capacity of the pump seeks to hit

18   the center of that envelope of operation, and, therefore, I

19   think it is the most appropriate number to use for used and

20   useful.

21        Q    Okay.  Would you agree though that there are times

22   that when two or more high service pumps are operated at the

23   same time they will have flow rates that are less than their

24   rated capacity?

25        A    I would say generally because of increased head

FLORIDA PUBLIC SERVICE COMMISSION

78

1   conditions in the discharge piping that is correct.

2        Q    Would you agree that operators may alternate the use

3   of multiple pumps depending on the demands of the system and

4   therefore not use all of the pumps at the same time?

5        A    That is quite possible.

6        Q    Do you agree with Mr. Redemann's statement in his

7   testimony that generally speaking the cost of high service

8   pumps is minimal compared to the cost of storage?

9        A    No, I disagree with that.  I believe it is certainly

10   less in almost all cases, but by no means do I think that it's

11   minimal.

12        Q    Do you agree that factors such as the configuration

13   of piping and the specific operation of high service pumps

14   should be taken into account in determining the effective

15   capacity of high service pumps if the Commission goes with a

16   separate used and useful methodology?

17        A    I believe that those considerations are done during

18   the design process, and that when an engineer designs a high

19   service pumping system, he does it knowing the operating

20   conditions of the system, the discharge piping and everything

21   that goes into it and designs the rated pumps at the

22   appropriate levels to be able to provide to serve that.  For

23   the, for calculations of used and useful, I believe that it is

24   appropriate to rely upon the engineer's original design and

25   utilize the rated capacity of the pumps.

FLORIDA PUBLIC SERVICE COMMISSION

79

1        Q    If the Commission were to go with a, a separate

2   formula in the rule for high service pumps, would you agree

3   that an appropriate formula would be to divide the greater of

4   the peak hour demand or maximum day demand plus fire demand and

5   gallons per minute by the reliable capacity of the high service

6   pumps?

7        A    To the extent that that generally follows what I

8   propose, yes.

9        Q    Do you agree that firm reliability, firm reliable

10   capacity of high service pumps should be determined by removing

11   the capacity of the pump with the highest capacity from the

12   total capacity of all pumps?

13        A    Yes, I do.

14        Q    Do you agree that the reliable capacity of the

15   remaining pumps in my example should be determined with

16   consideration given to the fact that the rated capacity of each

17   pump may be more than the combined capacity of all pumps?

18        A    I'm sorry.  I'm not following you on that question.

19        Q    Okay.  When you're talking about -- this is assuming

20   if the Commission were to incorporate something in the proposed

21   rule that's not there now, which is sort of the formula for

22   high service pumps, and you're trying to determine the reliable

23   capacity, my question was do you believe that the -- do you

24   agree that the reliable capacity of the remaining pumps, we've

25   taken the highest one out of service, the remaining pumps

FLORIDA PUBLIC SERVICE COMMISSION

80

1   should be determined with consideration given to the fact that

2   the rated capacity of each pump may be more than the combined

3   capacity of all pumps when they're operated at the same time?

4        A    I do not.

5        Q    Do you agree that there may be limiting factors

6   attributable to the actual operation of the remaining pumps in

7   my example?

8        A    There could be limiting factors anywhere in a water

9   system.

10        Q    So that's a yes?

11        A    Once again, you know, an alternative methodology is a

12   way of handling those special cases.

13        Q    Let me switch to a different subject, Mr. Woodcock.

14   This is covered on Page 23 of your testimony.  It's essentially

15   the issue of maximum day demands and peak demands.  Would you

16   agree that if the maximum day has an unusual occurrence, that

17   it would only be logical and consistent to use the next highest

18   maximum day, so long as it does not have an unusual occurrence?

19        A    For purposes of calculating used and useful?

20        Q    Yes.

21        A    No.

22        Q    Are you aware of any national standard or design

23   criteria that would support defaulting to a five-day average?

24        A    No.  From a design standpoint, no.

25        Q    Once a maximum day is experienced for a water

FLORIDA PUBLIC SERVICE COMMISSION

81

1   treatment plant is there ever any real world justification for

2   using anything less than that maximum rate of flow even if the

3   test year maximum day is lower?

4        A    For purposes of design or used and useful?

5        Q    Used and useful.

6        A    Well, for used and useful there's an important

7   concept that's outside of design, which is you need to remain

8   within the test year so that everything submitted within the

9   rate case lines up within the same time period.

10             So to the extent that there is this overriding

11   matching principle that applies to rate cases in general, I

12   would say that the flows need to remain within the test year.

13        Q    So as I understand your testimony, you would ignore

14   the real world fact that, say, for example, the year before

15   flows were higher in order to have the matching of a test year?

16        A    I would say that is correct.  Provided to the

17   extent -- I guess let me qualify.

18        Q    Sure.

19        A    There is the alternative calculation provision.  I

20   mean, if there's some overwhelming good reason, there might be

21   a case to be made there.

22        Q    Okay.

23        A    That's one of the reasons why that provision needs to

24   be there.

25        Q    You would agree though that design criteria for a

FLORIDA PUBLIC SERVICE COMMISSION

82

1   water treatment plant is never dependent on a Public Service

2   Commission's rate setting test year?

3        A    Correct.

4        Q    Okay.  Let me switch topics again, please.  Let me

5   ask you to go to Page 9 of your direct where you talk about the

6   peak demand for a water treatment system with and without

7   storage.

8             With respect to the, the issue of storage, do you

9   agree that storage is provided for equalization, fire

10   protection and emergencies?

11        A    I believe that it can be provided for that.

12        Q    Is that a yes?

13        A    In, in some cases, yes, those are all considerations

14   that you can make.

15        Q    Do you agree that storage facilities may be located

16   at various spots or locations throughout a distribution system?

17        A    Yes.

18        Q    Would you agree that if a fire occurs, that all

19   facilities are generally used at their full capacity, including

20   storage?

21        A    No.

22        Q    Would you agree that that can be the case depending

23   on whether there's one fire or multiple fires on a particular

24   system?

25        A    Or magnitude of fire, yes.  I mean, the size of the

FLORIDA PUBLIC SERVICE COMMISSION

83

1   system plays a role into that, the characteristics of the

2   service area, a lot of very specific cases.

3        Q    Yes, that can be the case.

4        A    It can be.  May not always be.

5        Q    Okay.  Let me ask you to turn to Page 17 of your

6   direct, please, beginning at Line 7.

7        A    I have to apologize.  My copy of my testimony does

8   not have Page 17.  If I could -- a problem with the copier, I

9   guess.

10        Q    We're working on that one.

11        A    Thank you, Steve.  Okay.

12        Q    Okay.  Let me, let me ask you to take a look at

13   Line 7 on Page 17.  Familiarize yourself with that, if you

14   will, Mr. Woodcock.

15             You've got a sentence there that starts with the

16   words, "This provision."  That's actually where I'm looking at,

17   and then just keep reading forward.

18        A    Do you mean the sentence that begins with "This

19   subparagraph"?

20        Q    It says, "This provision" -- I think you're referring

21   to Subsection (4)(a).  You say, "This provision provides

22   absolutely no standards or definition to the term 'minimum size

23   necessary.'"

24        A    Yes.

25        Q    Okay.  As I understand it then, if you keep reading

FLORIDA PUBLIC SERVICE COMMISSION

84

1   your testimony, the concern that you have is that there would

2   be significant amounts of subjective opinion testimony from

3   experts in rate cases as to what is meant by the term "minimum

4   size necessary." Is that a fair statement of what you're

5   saying?

6        A    That is correct.  The rule is seeking to kind of

7   streamline the process, and that kind of opens it up to a lot

8   of interpretation.

9        Q    Okay.  Now wouldn't you agree that for every issue or

10   provision in the proposed rule that the Commission may

11   ultimately decide to remove a section of the proposed rule and

12   throw into the alternative methodologies, that we have the same

13   implications, it's open season?

14        A    Well, to the extent that the rule is supposed to

15   provide guidelines on how to calculate it and recognizing that

16   there are special cases.  I mean, there has to be that

17   flexibility in there for special cases.  I would say that

18   putting a term like that in the body of the rest of the rule

19   which is supposed to simplify and streamline things is not

20   appropriate.  It could certainly be handled as an alternative

21   calculation or an alternative methodology to what's in the

22   rule.

23        Q    Every issue that the Commission does not put into

24   express rule language and basically says we don't need a rule

25   on this, this can be addressed in the alternative calculation

FLORIDA PUBLIC SERVICE COMMISSION

85

1   provisions, the implications of that are that there could be

2   future rate case proceedings where we'll have competing

3   experts; correct?

4        A    Yes.

5        Q    Let me ask you one more question about this phrase

6   "minimum size necessary."  Wouldn't you agree that with respect

7   to that phrase, "minimum size necessary," that there's really

8   nothing overly complicated for an engineer to determine if a

9   system is the minimum size necessary to serve existing

10   customers, plus growth, plus fire flow?

11        A    No, I don't agree with that at all.  I mean, I look

12   at minimum size necessary and I think to myself of what, within

13   what respect, you know, under what conditions?  Minimum size

14   necessary really tells me nothing, other than -- I mean, if you

15   were to say the number ten is your minimum, then that's

16   something I think everybody could agree upon.  But just minimum

17   size necessary provides very little clarity.

18        Q    Let me ask you a question or two on your testimony on

19   Page 22 on Line 23.  Your -- that's part of a discussion

20   regarding Subsection (7)(a) of the rule.

21        A    Okay.

22        Q    Okay.  You've got some, some proposed language there

23   that talks about for larger systems with a diverse customer

24   base.  Do you see that?

25        A    Uh-huh.

FLORIDA PUBLIC SERVICE COMMISSION

86

1        Q    Okay.  Wouldn't you agree that the term "diverse

2   customer base" is vague?

3        A    Yes.  Can I speak to my rebuttal testimony that

4   changes this?

5        Q    I think that the Chairman's ruling is that you can if

6   you're asked that question when you come up for your rebuttal.

7   I don't, I don't have anything further on that particular

8   topic.

9             Let me ask you to turn to Page 17 where you are

10   talking about Subsection (4)(b) of the proposed rule.

11        A    Okay.

12        Q    Is it your position that for a system to be

13   100 percent used and useful when it is built out there must

14   also be a showing that the system was designed prudently?

15        A    Yes.

16        Q    Your position is that one of the initial steps to

17   determining if a system was prudently designed is to perform a

18   used and useful calculation; isn't that right?

19        A    Yes, it is.

20        Q    Is it your testimony that engineers perform used and

21   useful calculations when they design distribution systems?

22        A    Design and used and useful are not correlated.  No,

23   they do not.

24        Q    They don't do that, do they?

25        A    No.

FLORIDA PUBLIC SERVICE COMMISSION

87

1        Q    Let's talk about fire flow for a moment,

2   Mr. Woodcock.  Let me ask you to go to Pages 11 and 12 of your

3   prefiled direct testimony.

4             Do you agree with Mr. Guastella's contentions that

5   local governmental authorities often recommend a rate of flow

6   per hydrant?

7        A    Yes.

8        Q    Do you agree that fire flow requirements need to be

9   met for an entire water system, taking into account the

10   population being served, not just an individual building?

11        A    Can you repeat the question?

12        Q    Yeah.  Do you agree that fire flow requirements for a

13   utility need to be met for the entire service area, the entire

14   water system, taking into account the population of the

15   community being served?

16        A    Okay.  One more time.  If you could repeat the

17   question.

18        Q    Sure.  Sure.  Do you agree that fire flow

19   requirements need to be met for an entire water system, an

20   entire service area, taking into account the population of the

21   community being served?

22        A    If there are fire flow requirements within that

23   community, it needs to be met to the extent that there are, you

24   know, fire flow requirements that are put on the developments

25   that are within that system.

FLORIDA PUBLIC SERVICE COMMISSION

88

1        Q    That would be a yes to my question then?

2        A    No, it's not.  It's actually a qualified yes to your

3   question.

4             When you're looking at fire flow requirements, you're

5   looking at developing -- you know, a system may come in and

6   have new fire flow requirements put upon it in different areas

7   of its service area.  I think it's very rare that you have an

8   open field and a fire flow requirement and a utility comes in

9   and says we're going to design everything to this fire flow

10   requirement.

11        Q    You agree, do you not, that a utility has to have

12   sufficient fire flow to address fires throughout its entire

13   service area, don't you?

14        A    I'm going to say that that is rarely the case.  That

15   may be the case.

16        Q    What's the answer to my question?

17        A    Not always.

18        Q    Would you agree that a water distribution system must

19   be properly designed and capable of meeting fire flow demands

20   throughout its entire service area, including instances where

21   there are multiple or coincidental fires?

22        A    I think that a water treatment system would be and is

23   typically designed based on the fire flow requirements that are

24   out there by the local government.  To the extent that they

25   include those types of multiple fire situations, then, yes.

FLORIDA PUBLIC SERVICE COMMISSION

89

1        Q    Would you agree that proper engineering design would

2   have a water distribution system capable of meeting fire

3   service requirements throughout the service area?

4        A    I believe you already asked me that question.  You

5   know, it's, it's a maybe.  Within a specific service area you

6   don't know what the specific fire flow requirements may be.  In

7   other words, there may have been none back in the 1960s when

8   the utility was created and, therefore, there are parts of that

9   system that have no hydrants and their lines are not sized to

10   provide service for fire.  There may be newer developments that

11   come in that do have a fire requirement, and in that case the

12   utility would need to provide that fire requirement.  But it's

13   not, it's not just as easy as the systemwide.  I think that's

14   what I'm having trouble with your, your question.

15        Q    Okay.  I just have a few more questions,

16   Mr. Woodcock.

17             The issue of unaccounted for water, would you agree

18   that all water systems experience water losses or unaccounted

19   for water?

20        A    Yes.

21        Q    Would you agree that as a water distribution system

22   gets old that water losses tend to go up but that the original

23   cost of the system obviously does not change?

24        A    Yeah.  Provided there's no reinvestment into that

25   system you could safely make that statement.

FLORIDA PUBLIC SERVICE COMMISSION

90

1        Q    Would you agree that water systems are expected to be

2   able to meet maximum demands in addition to water losses?

3        A    Can you repeat that question again?

4        Q    Would you agree that water systems are expected to be

5   able to meet maximum demands in addition to water losses?

6        A    Well, they are designed to meet maximum day or

7   maximum demands, let's say, peak demands, whatever the basis

8   is.  Typically in the design process I have never come across a

9   case where you're automatically building in, oh, we're going to

10   lose 10 percent of our water.

11        Q    In a real world though doesn't a water distribution

12   system sort of have to account for its water system losses and

13   still be able to meet the maximum demands of the customer base?

14        A    Yes.

15             MR. HOFFMAN:  No further questions.  Thank you,

16   Mr. Woodcock.

17             THE WITNESS:  Thank you.

18             CHAIRMAN CARTER:  Commissioners, any questions?

19   Commissioners?  Mr. Friedman, you're recognized.

20             MR. FRIEDMAN:  Thank you.

21             CHAIRMAN CARTER:  Then I'll come back to staff.

22                          CROSS EXAMINATION

23   BY MR. FRIEDMAN:

24        Q    Mr. Woodcock, can you see me way down here?

25        A    I can.

FLORIDA PUBLIC SERVICE COMMISSION

91

1        Q    Okay.  As an engineer have you designed water

2   facilities?

3        A    Yes, I have.

4        Q    And have some of these water facilities that you've

5   designed been for private utilities regulated by the Public

6   Service Commission?

7        A    Yes, I have.

8        Q    And in designing those systems did you take into

9   consideration the Public Service Commission's policies on used

10   and useful in existence at that time?

11        A    The systems that I worked on for investor-owned

12   utilities in my career was very early on.  I was one of a

13   number of engineers on the project.  I was not the overall

14   project manager.  So I will answer your question by saying, no,

15   not to my knowledge on those systems.

16        Q    And so isn't it true that the systems that you

17   designed might never be 100 percent used and useful as the

18   Public Service Commission may determine?

19        A    I would have no knowledge about that for those

20   systems.

21        Q    What systems did you design?

22        A    The ones that come to the top of my head are the

23   Venice Gardens utility systems for Southern States Utilities

24   and the Burnt Store Water Treatment Plant for Southern States

25   Utilities.  I believe that those are the only two that I've

FLORIDA PUBLIC SERVICE COMMISSION

92

1   been a part of for an investor-owned utility.

2        Q    And so when you were designing those systems, you

3   didn't pay any consideration to a used and usefulness of those

4   from a regulatory standpoint?

5        A    I was not in a position as an engineer on those

6   projects.  I was one of several engineers.  I was not the

7   project manager, so I do not know.  I know that I personally

8   did not, but I had a very small part of those projects.  I was

9   not the lead design engineer, I wasn't the contact with the

10   client.  I don't know what went on as far as the specific

11   sizing of those facilities.  I was putting specifications

12   together and blueprints.

13        Q    But in none of the meetings that you went to was the

14   concept of used and usefulness discussed when designing the

15   systems.

16        A    You know, I would say for those two meetings -- I

17   mean, they were done in the first couple -- or for those two

18   projects that were done in the first couple of years of my

19   experience as an engineer I don't even think I went to any

20   client meetings.

21        Q    How about meetings just among the engineering group

22   itself, did the issue of used and usefulness, was that concept

23   discussed in the design?

24        A    Not to my recollection.

25        Q    You didn't have any courses on used and useful in

FLORIDA PUBLIC SERVICE COMMISSION

93

1   your engineer school, did you?

2        A    I did not.  Used and useful is not really an

3   engineering concept.

4        Q    Okay.  It's just a utility ratemaking concept, is it

5   not?

6        A    Correct.

7        Q    Now if a system has no storage -- this goes to the

8   issue you were discussing with Mr. Hoffman about the well pump

9   in some instances being the high service pump.  Do you remember

10   that discussion?

11        A    Yes.

12        Q    Okay.  And so if a system has no storage and the well

13   pumps act as the high service pumps, under your rule proposal

14   would you evaluate for used and usefulness for the well pumps

15   and treatment pumps be under the treatment plant rule or the

16   high service pump proposal?

17        A    In the way that my testimony is worded and the

18   exhibit that is attached to my direct testimony it would be

19   done as a well pump for a system without storage.

20        Q    So you wouldn't, you wouldn't, you would not evaluate

21   it separately as a high service pump.

22        A    The -- in my mind, in the intent in what I have

23   proposed in my testimony, those calculations would be

24   identical.

25        Q    Okay.  In systems that have -- let's start with

FLORIDA PUBLIC SERVICE COMMISSION

94

1   systems that have no storage.  Is there sufficient demand 24

2   hours a day, seven days a week for 365 days a year to run those

3   pumps?

4        A    For systems without storage?

5        Q    Correct.

6        A    Is there enough demand to keep them running 24 hours

7   a day, 365 days a year?

8        Q    That's correct.

9        A    No.  For a, a system that does not have storage,

10   those pumps have to be sized based on what the peak hour demand

11   is.  Therefore, those pumps will be sized to be able to provide

12   that peak hour and will run consistently for that peak hour.

13   Throughout the rest of the course of the day they will come on

14   intermittently in order to provide whatever the demand is on

15   the system.

16        Q    Now even with systems with storage, isn't it true

17   that there isn't sufficient demand 24 hours a day, seven days a

18   week, 365 days a year to run those pumps continuously?

19        A    Are we talking about the well, the well pumps?

20        Q    That's correct.

21        A    Okay.  For water treatment systems with storage there

22   is not demand to run the well pumps, which would be sized based

23   on maximum day to keep them running 24/7/365.

24        Q    Now I understand that you're recommending some

25   language be added in the section dealing with excessive

FLORIDA PUBLIC SERVICE COMMISSION

95

1   unaccounted for water that would require that the document,

2   that there be documentation for line flushing, fire fighting

3   and line breaks, that it be documented by complete records?

4        A    Yes.

5        Q    And is the term "complete records" an engineering

6   concept that we can look to a definition of what that is?

7        A    I would say not.

8        Q    So wouldn't you agree that as to the term "complete

9   records," that different people equally qualified could have

10   different definitions of that term?

11        A    Yes.

12        Q    Doesn't the Public Service Commission already have a

13   rule that places the burden of proof on the utility to prove

14   each schedule of its minimum filing requirements?

15        A    I don't know specific knowledge of that, but, yes, I

16   believe that is the case.

17        Q    And isn't the used and useful calculation a schedule

18   in the minimum filing requirements?

19        A    Yes.

20             MR. FRIEDMAN:  That's all the questions we have.

21   Thank you.

22             CHAIRMAN CARTER:  Thank you.

23             Commissioner Argenziano.

24             COMMISSIONER ARGENZIANO:  Thank you, Mr. Chair.  Just

25   a couple of questions real quick.

FLORIDA PUBLIC SERVICE COMMISSION

96

1             Why does 24-hour pumping make sense to you as an

2   engineer?

3             THE WITNESS:  As far as the well fields go?

4             COMMISSIONER ARGENZIANO:  Uh-huh.

5             THE WITNESS:  Well, number one, you want to look to

6   get essentially the most bang for your buck.  If you're going

7   to sink a well in the ground, you're going to want to run it

8   for as long as you can.

9             Now keep in mind that if you're designing a water

10   system, that well field is going to be based probably on

11   maximum day, let's say.  So it's only going to be running 24

12   hours for one day out of a year.  But, you know, essentially

13   what we're looking to do as an engineer is to, you know, get

14   the most for what we have to build, and so 24 hours kind of

15   becomes the default.

16             COMMISSIONER ARGENZIANO:  Well, would you take into

17   consideration then or should you take into consideration

18   configuration of the piping and so on that I've heard before?

19             THE WITNESS:  It's generally done when you're looking

20   at sizing those well pumps and what they can be capable of

21   delivering.  In other words, you would be -- you would pick,

22   design and install a well pump that would be able to handle a

23   multiple pump configuration.

24             COMMISSIONER ARGENZIANO:  And if I would, forgive my

25   ignorance, wouldn't that be done before you sink the wells in

FLORIDA PUBLIC SERVICE COMMISSION

97

1   the design process?

2             THE WITNESS:  Oh, absolutely.  It's part of the

3   design process.  Yeah.  And it also plays into sizing the wells

4   also, the well hole itself.

5             COMMISSIONER ARGENZIANO:  Okay.  Well, then after the

6   fact if you're going to implement 24-hour pumping, how would

7   you take that into account if they weren't designed that way?

8             THE WITNESS:  I'm sorry?

9             COMMISSIONER ARGENZIANO:  Maybe I'm not saying it

10   right.  If the wells were already -- the design process is

11   done, the wells are in, and now you're going to run the pumps

12   24 hours a day but they weren't designed that way, how would

13   you accommodate for that now?

14             THE WITNESS:  Okay.  If, if the wells weren't

15   designed for 24 hours a day, and we're making that supposition

16   that we designed them for --

17             COMMISSIONER ARGENZIANO:  Right.

18             THE WITNESS:  Right, that they're only going to --

19   and this is --

20             COMMISSIONER ARGENZIANO:  Or if I restate that.

21   Maybe it -- if that was the case, then that would have to be

22   taken into account if you were going to implement a rule that

23   said 24-hour pumping.

24             THE WITNESS:  Yes, I would say that it would.  Yes.

25             COMMISSIONER ARGENZIANO:  Okay.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

98

1             CHAIRMAN CARTER:  Commissioners, any further

2   questions?

3             Staff, you're recognized.

4             MS. GERVASI:  Thank you, Commissioner.  We do have

5   some questions for Mr. Woodcock, but I wonder if we could take

6   maybe a five-minute break so that staff can consolidate those

7   questions.  We want to make sure we don't ask repetitive

8   questions.

9             CHAIRMAN CARTER:  I'm looking at the clock on the

10   wall, Commissioners.  What say we come back at 11:30.

11             MS. GERVASI:  Thank you.

12             CHAIRMAN CARTER:  11:30?  Okay.  We're on break.

13             (Recess taken.)

14             We are back on the record for our hearing, and,

15   staff, you're recognized.

16             MS. GERVASI:  Thank you.

17                          CROSS EXAMINATION

18   BY MS. GERVASI:

19        Q    Good morning, Mr. Woodcock.

20        A    Good morning.

21        Q    Would you please turn to Page 9 of your prefiled

22   direct testimony and take a look at Lines 12 through 21 of Page

23   9.

24        A    Okay.

25        Q    Here you discuss peak demand for a water treatment

FLORIDA PUBLIC SERVICE COMMISSION

99

1   system without storage; is that correct?

2        A    That is correct.

3        Q    Why do you include fire flow in the maximum day

4   demand but you don't include fire flow in the maximum hour

5   demand?

6        A    Well, when you're evaluating high service pumps or in

7   this case well pumps without storage, you do it on a two-prong

8   test.  Number one, peak hour, you want to meet that highest

9   peak in the day on the maximum day out of the year.  That's one

10   thing that the high service pumps need to do.

11             When you're looking at a system that has a fire flow

12   requirement, you also want to look at what that impact of the

13   fire flow requirement might be on the facilities.  DEP

14   recommends that you look at fire flow as a peaking factor for

15   facilities with a background demand of maximum day.  So when

16   we're evaluating water treatment systems that do not have

17   storage where the well acts as high service, we take the

18   two-pronged approach, we look at both cases.  It's going to be

19   either the greater of either the peak hour demand or the

20   maximum day plus fire flow.  And this is in recognition of the

21   fact that sometimes fire flows can be way greater than peak

22   demands in a system, and so you want to make sure that you've

23   got your bases covered on fire flow.

24        Q    If there's a fire and the water system does not have

25   storage, where does the water come from to extinguish the fire?

FLORIDA PUBLIC SERVICE COMMISSION

100

1        A    If there is a fire and the water system doesn't have

2   storage, it would have to come from the well pumps.

3        Q    And where does the fire flow come from if, if it

4   occurs during peak periods, if the fire occurs during peak

5   periods?

6        A    Peak periods as in the peak hour demand, is that what

7   you're getting at?

8        Q    Yes.

9        A    Okay.  Well, number one, you're looking at the

10   possibility of a fire occurring during the largest, the peak

11   hour of the peak day of the maximum day out of the year.  When

12   you're designing facilities, you kind of have to weigh a risk

13   there regarding, you know, what is the likelihood of that

14   actually happening versus sizing, oversizing your facilities.

15   That's why the standards that I'm presenting here, which are

16   also DEP standards for sizing high service pumps, kind of

17   incorporate the language that I have embodied here.

18             Secondly, I would say that when you're looking at a

19   fire occurring in the peak hour, typically you're going to see

20   a lot of demand being placed on the system.  What that does is

21   essentially lower the system pressure.  When you're looking at

22   lower system pressures, you're not basically getting as much

23   water out of any given faucet as you normally would because a

24   lot of it's going to the hydrants.  So I would say that having

25   a fire on your peak hour would tend to suppress the impact of

FLORIDA PUBLIC SERVICE COMMISSION

101

1   your peak hour on the system.

2        Q    Would you agree that in the event of a fire in a

3   system that does not have storage that the fire flow would have

4   to come from the wells if the fire occurs during peak periods?

5        A    Yes, it would have to come from the wells.  Yes.

6        Q    Thank you.  Please turn to Page 12 of your direct

7   testimony, and take a look at Lines 10 through 14 of Page 12.

8        A    Okay.

9        Q    And here you discuss peak demand for storage;

10   correct?

11        A    Yes.

12        Q    And you're recommending that 25 percent of the

13   utility's maximum day demand be used as peak demand for

14   storage; right?

15        A    Plus an allowance for fire flow, if, if required, if

16   provided.

17        Q    Would you apply the 25 percent maximum day storage to

18   any type of water treatment plant regardless of whether it's a

19   line softening, reverse osmosis, an ion exchange, et cetera,

20   any type of water treatment plant?

21        A    Yes.  Storage basically comes after your major

22   treatment process, and the demands that are placed from the

23   system, you know, kind of start with that storage tank.  So,

24   yeah, you would generally size storage tanks the same

25   regardless of what the upstream treatment process might be.

FLORIDA PUBLIC SERVICE COMMISSION

102

1        Q    Thank you.  Do you agree that the 25 percent maximum

2   day storage is for flow equalization?

3        A    I do.

4        Q    Do you believe that an allowance of 25 percent of the

5   peak demand for storage allows for emergencies such as pipe

6   failures, major trunk main failures, equipment failures, et

7   cetera?

8        A    Well, to the extent you have those in your system and

9   they're going to be pulling from your storage tank, yes, it

10   does.

11        Q    Is it your experience that your 25 percent of peak

12   demand proposal reflects how storage facilities are designed

13   for new water systems?

14        A    It is in accordance with the current FDEP rules.

15   Yes.

16        Q    Thank you.  Please turn to Page 14 now of your direct

17   testimony on Lines 10 through 12 of Page 14.  Here you

18   recommend that any water claimed as accounted for that was used

19   for flushing, fire fighting and water lost through line breaks

20   must be documented by complete records of these flow losses.

21   And I know we discussed -- you've discussed this somewhat in

22   previous questioning.  We're interested in knowing what

23   specific documentation you would recommend that the rule

24   require.

25        A    Well, it's going to vary from system to system and

FLORIDA PUBLIC SERVICE COMMISSION

103

1   it's also going to vary depending upon what type of accounting

2   there is of the water.  Number one, for routine line flushing I

3   would expect to see, you know, daily flushing logs of, you

4   know, what valve was open, how long was it flushed for, what is

5   the estimate?  Some type of contemporaneous thing.

6             For fire hydrant testing I would expect the same

7   thing.  For fire flows I'd expect some estimate of what the

8   fire -- what volumes were withdrawn from the system in order to

9   fight the fire.

10        Q    Are you aware that the DEP requires documentation of

11   unmetered water uses by way of a line entry on a company's

12   monthly operating report or water plant daily log?

13        A    You know, I can't say that I have seen that.

14        Q    Okay.  Would you agree that in dollars the

15   unaccounted for water adjustment that is typically made in a

16   water rate case is small if any adjustment is needed?

17        A    I can't say I've been involved in a lot of rate cases

18   to be able to say what typically happens.

19        Q    Thank you.  Are you aware that if there have been no

20   known changes to a water system and the water system was

21   100 percent used and useful previously, in a previous rate

22   case, that the Commission has found that that system should be

23   100 percent used and useful again in the next rate case or in

24   the current rate case?

25        A    And your question is am I aware of that?

FLORIDA PUBLIC SERVICE COMMISSION

104

1        Q    Yes.

2        A    I am not aware of that.  I think that it's also very

3   highly unlikely you're going to have a system that has done

4   nothing:  No demand patterns changed, no anything happen to a

5   system in between rate cases.  I would think that is an

6   unlikely event.

7        Q    So you're not aware that, for example, if the water

8   flow from the last rate case was reduced due to conservation

9   and the system was found to be 100 percent used and useful in

10   that previous case, that the Commission would find the system

11   to again be 100 percent used and useful the next time around,

12   in the next rate case?

13        A    Well, I would say, you know, are those conservation

14   efforts long-term?  You know, maybe it's gone back up, maybe

15   it's reduced further.  It would be hard to tell without

16   starting at least the used and useful process over again as

17   part of a new rate case.

18        Q    Thank you.  Please turn to Page 18 of your direct

19   testimony at Lines 9 through 12.  And here you state that when

20   there is only one well, the used and useful calculation should

21   be based on the capacity of that single well; correct?

22        A    Correct.

23        Q    And then also on Page 18 at Lines 14 through 17 you

24   state that removing the largest well from service is an

25   acceptable way to calculate used and useful for multiple well

FLORIDA PUBLIC SERVICE COMMISSION

105

1   systems; however, for single well systems there is not a

2   redundant, standby well that can be removed, and in these cases

3   the used and useful should be evaluated on the single well in

4   service; correct?

5        A    Correct.

6        Q    Have you ever designed a water system in Florida that

7   has, that had only one well?

8        A    I'm going to say that I am not sure because I think

9   there might be one case where I did, and that was the East

10   Palatka Water System.  I can't remember if we had two wells on

11   that or not.

12        Q    Thank you.

13        A    It was a very small system.

14        Q    Are you aware of the Commission's practice to

15   consider systems with one well or one high service pump to be

16   100 percent used and useful?

17        A    I'm aware of that practice, I guess, to the extent

18   that it's in the proposed rule.

19        Q    Thank you.  If you would please turn to Page 21 of

20   your direct testimony at Lines 9 through 12.

21        A    Okay.

22        Q    And here you state that the DEP rules for public

23   water supply wells make no specific reference to a requirement

24   that would require that well pumps be limited to 12 hours of

25   pumping per day if the system includes storage.  And you say

FLORIDA PUBLIC SERVICE COMMISSION

106

1   that prudent and efficient design of a well system would seek

2   to maximize the pumping time to the daily maximum of 24 hours;

3   right?

4        A    Correct.

5        Q    Do you agree that water plants do not provide

6   constant flow for 24 hours a day?

7        A    They provide the demands that are on the system for

8   24 hours a day.  Sometimes they can be for 24 hours a day.  You

9   can always have some draw on your utility system.

10        Q    You do agree that there are peak periods during the

11   day; right?

12        A    Yes, there are peak periods during the day.

13        Q    How would running the well pumps 24 hours a day

14   affect the used and useful life of those pumps?

15        A    How would running the pumps 12 hours a day affect the

16   used and useful life of the pumps?

17        Q    How would running them 24 hours a day affect the

18   usefulness or the useful life of those pumps?

19        A    The useful life.  Okay.  Well, number one, keep in

20   mind they'll never be operating 24 hours a day, seven days a

21   week, 52 weeks a year.  If the system is properly designed, you

22   know, they're going to be operating, you know, 24 hours a day

23   maybe on a max day.

24             I really don't think I can give you a clear

25   definition on, on your specific question simply because pumps

FLORIDA PUBLIC SERVICE COMMISSION

107

1   like to operate when they're turned on and they like to keep

2   running.  One of the hardest stress points on the mechanics of

3   a pump is when it gets turned on, when all the still things are

4   actually getting innervated and pulling together.  So you have

5   a situation where running it longer over longer periods of time

6   may actually be more advantageous than having it start, stop,

7   start, stop a lot.  By the same token, I would say, you know,

8   just like you run a car forever, maybe the reverse case could

9   be true.  I could make an argument both ways on that.

10        Q    Thank you.  I have only a few remaining questions for

11   you and they concern high service pumping costs.  If you would

12   please take a look back at Page 7 of your direct testimony.  At

13   Lines 20 and 21 of Page 7 you state that high service pumps

14   after storage are separate and distinct components from both

15   water treatment and storage; correct?

16        A    Correct.

17        Q    Would you agree that ground storage and high service

18   pumps are designed to work together and are usually designed

19   and installed at the same time?

20        A    They are designed to work together in the sense that

21   everything in a water treatment plant has to work together and

22   be designed appropriately, accordingly.

23             You can have increases in your high service pumping

24   capacity without increasing your pumps.  They don't necessarily

25   always have to be constructed together.

FLORIDA PUBLIC SERVICE COMMISSION

108

1        Q    In your experience have you seen any instances where

2   a water system's high service pumps were significantly

3   oversized in anticipation of future storage expansion?

4        A    I cannot say that for the pumps themselves.  Usually

5   when you have that type of a situation you would leave a blank

6   spot to put in an extra pump in the future.

7        Q    Thank you.  Would it be more cost-effective for a

8   utility to install a single storage facility to meet its peak

9   demand or to add storage periodically as needed?

10        A    Well, that's a difficult question to answer.  It

11   depends on, you know, the economics of it.  There may be

12   economies of scale in getting a larger tank.  You know, you

13   have -- if tanks are built with steel, steel prices fluctuate

14   wildly so you may see your costs go up or down in the future.

15   You're actually going to be using up more of a site if you have

16   multiple tanks.  That's kind of a hard determination to make in

17   general.

18             MS. GERVASI:  Thank you.  We have no further

19   questions.  Thank you.

20             CHAIRMAN CARTER:  Commissioners?  Commissioner Skop,

21   you're recognized.

22             COMMISSIONER SKOP:  Thank you, Chairman Carter.

23             Just trying to collect my thought on one question

24   that arose.  I was wondering if -- I know that there's been a

25   lot of discussion that the theoretical capacity of the pump

FLORIDA PUBLIC SERVICE COMMISSION

109

1   should be included in the denominator as opposed to the 12

2   hours.  So I was wondering if Mr. Woodcock, if he -- if the

3   terminology in terms of "firm reliable capacity" was maybe

4   expressed differently in terms of some other language, would

5   your testimony still be the same to the extent that you feel

6   that -- well, I've heard conflicting testimony.  What I think I

7   hear is that, again, the design is based on the theoretical

8   maximum that the pumps will operate at their most efficient

9   point for 24/7 pumping the capacity through the distribution

10   system.  And the tension here seems to be between -- that

11   what's theoretical doesn't really relate in a ratemaking idea

12   to what the actual or expected utilization of those pumps are

13   going to be.  But the term we're using is "firm reliable

14   capacity," which kind of takes out the biggest pump, assuming a

15   failure, to get some sort of reliability type index, if you

16   will.

17             I'm wondering, and, again, this is my question, if it

18   was not defined as "firm reliable capacity" and it was just

19   defined maybe something differently, maybe perhaps expected

20   flow or expected normal or something like that, would your

21   testimony be different to the extent that you would back away

22   from the 24-hour requirement and support the 12?

23             THE WITNESS:  I would have to say, no, it would not

24   change my testimony.

25             COMMISSIONER SKOP:  And can you offer a reason for

FLORIDA PUBLIC SERVICE COMMISSION

110

1   that?

2             THE WITNESS:  Well, I'm not quite sure I 100 percent

3   follow you.  But I guess in one sense it's not necessarily a

4   matter of semantics like how we word it.  I mean, there's a

5   design consideration that's at stake here.

6             If you design a well system, let's say there are

7   three wells, you're going to design it so that two of those

8   wells are going to be able to meet your maximum demands.

9   They're not going to operate 24/7 365 days a year.  They're

10   going to operate maybe 24 hours a day on that maximum day and

11   there's an additional pump here that we have out of service.

12             And when you go in and you're designing a well field,

13   that's what you look for them to do.  You recognize that those

14   pumps will be operating 24 hours a day on that max day.  If you

15   were to design them for, in order to operate 12 hours a day on

16   that maximum day, you'd essentially need to double the size of

17   all of your pumps in order to incorporate that.

18             So the real crux of the matter here that I have is

19   that we've got a whole factor of two that is, that is

20   determining how used and useful is going to be calculated with

21   respect to water treatment systems.

22             COMMISSIONER SKOP:  And thank you.  And, Mr. Chair,

23   just as a brief follow-up.  And I do appreciate that because, I

24   mean, as I understood, and I'm also an engineer, you know,

25   certainly the design characteristics, you need to take into

FLORIDA PUBLIC SERVICE COMMISSION

111

1   account the maximum hourly flow and peak demands and fire flow,

2   factor safety and maybe some growth margin and a provision for

3   the fact that the pumps and the piping may not operate as

4   efficiently through their expected useful life as they would

5   when they're brand new and clean.

6             But I guess what I'm struggling with is from a

7   ratemaking perspective, looking at what's fair, to the extent

8   that just because you have to build something that is for the

9   worst-case scenario and maybe oversized to some degree doesn't

10   necessarily mean it's going to operate at that, you know, at

11   that maximum design point all the, all the time.  And so I

12   think that that seems to be in my understanding what the

13   tension here is between OPC and the, and the utilities.  And,

14   again, I'm just trying to flush that out for my own reasoning.

15   But I was just wondering -- again, it occurred to me whether it

16   was a matter of the definition controlling the testimony in

17   terms of "firm reliable capacity," because I could see

18   arguments both ways on that just based on the wording as

19   opposed to if it wasn't defined like that, whether you would

20   back away.  And I think the answer was no for the reasons you

21   articulated, so thank you.

22             CHAIRMAN CARTER:  Thank you, Commissioner.

23             Commissioner Argenziano.

24             COMMISSIONER ARGENZIANO:  Just one other question.

25   And if considering 24-hour, allowing 24-hour pumping to take

FLORIDA PUBLIC SERVICE COMMISSION

112

1   place in the rule, should one consider -- or do you know if the

2   older systems are capable or if they were designed or -- I'm

3   trying to figure out in my mind if the rule were to change for

4   24 hours, how many systems were designed that way or --

5             THE WITNESS:  Let me reverse the question a little

6   bit and say I know of no system that has been sized on just 12

7   hours of pumping.

8             COMMISSIONER ARGENZIANO:  Okay.

9             THE WITNESS:  I know every system that I've been

10   involved in and when I evaluate systems, not just in used and

11   useful, but for master plans and for other engineering

12   situations, you know, we look at taking one pump out of service

13   and then we're saying, okay, this is the maximum your well

14   field can supply and have that go over 24 hours.

15             COMMISSIONER ARGENZIANO:  Thank you.

16             CHAIRMAN CARTER:  Is your -- just kind of a -- when

17   you're saying 24 hours, you're saying that it may, it should be

18   prepared to go 24 hours at the time that it's needed for that

19   one -- I think you said it may be once a year for that peak

20   period; is that right?

21             THE WITNESS:  That is correct.

22             CHAIRMAN CARTER:  But not as a general rule because

23   they don't run at 24 hours.

24             THE WITNESS:  Yeah.  No.  You would very rarely see

25   an entire well system running at 24/7 because the demands are

FLORIDA PUBLIC SERVICE COMMISSION

113

1   always going to be up and down throughout your system.  It

2   would be designed for that maximum case situation.

3             CHAIRMAN CARTER:  Okay.  Thank you.  Before I go back

4   to the parties, Commissioners, any further questions?

5             Okay.  Mr. Reilly.

6             MR. REILLY:  Very few.  I guess --

7             MR. FRIEDMAN:  Chairman Carter, I want to raise, I

8   want to raise an objection to Mr. Reilly conducting redirect

9   examination.  During Mr. Woodcock's deposition -- during his

10   testimony I had noticed Mr. Reilly writing notes.  During the

11   intermission Mr. Reilly took those notes, went over in the

12   corner and talked to this witness, and it's inappropriate to do

13   that.  And typically when that has happened courts have

14   sanctioned the party by not allowing them to have redirect

15   examination, and I think that's appropriate here.  It is very

16   inappropriate to discuss with your witness proposed redirect

17   testimony.  And I have reason to believe since Mr. Reilly had

18   that pad in front of him and was talking with Mr. Woodcock for

19   quite a while that that was discussed, and that's

20   inappropriate.

21             CHAIRMAN CARTER:  Mr. Reilly.

22             MR. REILLY:  I was not talking to him for quite a

23   while, and I did begin to say that I was going to ask him

24   redirect.  And so what I've done is -- and he said, "You

25   shouldn't be talking to your witness."  And I said, "Yes,

FLORIDA PUBLIC SERVICE COMMISSION

114

1   you're right," and then I stopped.  And so I have not asked any

2   redirect questions on either of those subjects.  I didn't

3   suggest any answers.  I said, "I was going to ask you redirect

4   on these two things."  And so in light of his comments, I am

5   not posing those redirect questions basically.  So then the

6   conversation ended.  And I have really only a couple of

7   questions.

8             MR. FRIEDMAN:  I think even what he did, telling him

9   what questions he was going to ask is inappropriate.

10             MR. REILLY:  Well, and I think that point is

11   well-taken and those are questions that I'm not posing.  So

12   that's --

13             CHAIRMAN CARTER:  Let's tread lightly, Mr. Reilly.

14             MR. REILLY:  Okay.

15             CHAIRMAN CARTER:  And, and as we tread lightly, let's

16   remember the rulings made earlier.

17             MR. REILLY:  All right.

18                        REDIRECT EXAMINATION

19   BY MR. REILLY:

20        Q    Mr. Woodcock, you were asked by Utilities, Inc. about

21   how you would calculate used and useful for high service

22   pumping.  I think your answer was that you would calculate it

23   the same as treatment; is that correct?

24        A    For high service pumping without -- same as treatment

25   without storage, I believe.

FLORIDA PUBLIC SERVICE COMMISSION

115

1        Q    Without storage.  And my question is how would you

2   calculate peak hour demand and maximum day demand for high

3   service pumping?  Would it be the same as treatment or in some

4   other way?

5        A    Yes.  I would, I would calculate it the same.

6        Q    The only other question -- let's see.  I think you

7   were also asked, "Do engineers do a used and useful calculation

8   when they're designing a system?"  And I think your answer was,

9   "No, they don't generally do a used and useful calculation when

10   they're designing a system."

11        A    Correct.

12        Q    And my question to you as a follow-up is what, what

13   do engineers properly do to try to match what they're building

14   with the anticipated demand?

15        A    Well, number one, if you're looking at designing an

16   expansion to an existing system, you've got a pretty good idea

17   of what the existing customer base is and what those flows are,

18   and so you would, you would size your system based on similar

19   flows.  You have a pretty good idea of what actually is going

20   to happen there.

21             In the event where you are building a new system, you

22   would use some design standard.  If you were building it from

23   the ground up, had no customers, you would use a design

24   standard to size the first phase of your facilities.

25             MR. REILLY:  Okay.  And the last matter is a matter

FLORIDA PUBLIC SERVICE COMMISSION

116

1   I'd almost yield to the Commission to give me some guidance

2   because as I was, I was talking to him during the break, I said

3   he had questions about the minimum, you know, that high service

4   pumps don't cost very much, it was very minimal.  And at that

5   point I said, you know, I don't even know what his answer is

6   going to be.  But, I mean, to the extent that he would -- I was

7   going to ask him a question about to the extent he could expand

8   on the cost of high service pumping.

9             CHAIRMAN CARTER:  Let's don't do that.  Let's don't

10   do that.  Let's, let's --

11             MR. REILLY:  Okay.  Then I'll leave, I'll leave that

12   one alone.

13             CHAIRMAN CARTER:  Yeah.  Let's leave that alone.  I

14   think -- and I've been -- and I want to give you as much

15   latitude as possible, but I have to respect the procedure and

16   the process.

17             MR. REILLY:  And that's fine.  Then that concludes

18   those few comments.

19             CHAIRMAN CARTER:  Mr. Hoffman.

20             MR. HOFFMAN:  Mr. Chairman, if we could just get a

21   point of clarification.  In Mr. Reilly's redirect first

22   question, I think the witness gave an answer with respect to

23   how he would calculate high service pumping.  And I just want

24   to make sure that, that the witness was not effectively saying

25   that he would calculate high service pumping in the manner set

FLORIDA PUBLIC SERVICE COMMISSION

117

1   forth in the revised exhibit which the Chairman has excluded

2   from the record.  Because I think he testified that he would

3   calculate it in the same way as a well, and I'm just not sure

4   if that's a different way of trying to get into the record a

5   subject that you have already excluded from the record.  So

6   perhaps we could get some clarification.

7             CHAIRMAN CARTER:  Mr. Woodcock, you were here when I

8   made the ruling, were you not?

9             THE WITNESS:  Yes, I was.

10             CHAIRMAN CARTER:  And you did not violate the ruling,

11   did you?

12             THE WITNESS:  I did not.

13             CHAIRMAN CARTER:  Okay.  I'll take the witness at his

14   word.

15             MR. HOFFMAN:  Thank you, Mr. Chairman.

16             CHAIRMAN CARTER:  Okay.  Any further questions for

17   this witness, any of the parties?

18             Now we do have the matter of Exhibit 2, which is

19   ATW-1.  I'll give the parties an opportunity to look at that.

20             MR. FRIEDMAN:  No objection.

21             CHAIRMAN CARTER:  No objections.

22             MR. HOFFMAN:  No.

23             CHAIRMAN CARTER:  No objections.

24             MR. REILLY:  Let me clarify.  It's my understanding I

25   have offered into evidence only ATW-1.  I don't think it's

FLORIDA PUBLIC SERVICE COMMISSION

118

1   helpful to at this time submit ATW-2 as filed with his direct

2   testimony because it's quite dated.  And so this helpful single

3   place area that I wanted everyone to look at for our suggested

4   changes is not useful anymore because it's been, it's been

5   ruled -- so I don't think it's helpful.  So the only, the only

6   exhibit I am moving into the record at this time is ATW-1.

7             CHAIRMAN CARTER:  What I was doing, Mr. Reilly, we

8   normally after the testimony, direct and cross of a witness, we

9   usually admit the exhibit.  And I was just giving the parties

10   an opportunity to say whether or not they had objections, and

11   there are no objections on our Exhibit 2 which is marked as

12   ATW-1.  Show it moved in.

13             (Exhibit 2 admitted into evidence)

14             Call your next witness.  Is that -- that's your only

15   witness, Mr. Reilly?

16             MR. REILLY:  That is our only witness.  Yes.

17             CHAIRMAN CARTER:  Mr. Hoffman, I think you're

18   recognized.

19             MR. HOFFMAN:  Thank you, Mr. Chairman.  Aqua

20   Utilities Florida would call John Guastella.

21             CHAIRMAN CARTER:  By the way, Mr. Woodcock, you are

22   excused.  So if you have to catch a flight or something --

23             MR. REILLY:  No.  He has rebuttal testimony, too.

24             CHAIRMAN CARTER:  Rebuttal?

25             MR. REILLY:  Yes.

FLORIDA PUBLIC SERVICE COMMISSION

119

1             CHAIRMAN CARTER:  Okay.  Well, then don't catch a

2   flight.  Catch a snack.

3                          JOHN F. GUASTELLA

4   was called as a witness on behalf of Aqua Utilities Florida

5   and, having been duly sworn, testified as follows:

6                         DIRECT EXAMINATION

7   BY MR. HOFFMAN:

8        Q    Would you please state your name and your business

9   address?

10        A    John F. Guastella, 6 Beacon Street, Suite 410,

11   Boston, Massachusetts.

12        Q    Mr. Guastella, you've been sworn, have you not?

13        A    I have.

14        Q    By whom are you employed?

15        A    Guastella Associates.

16        Q    And in what capacity?

17        A    I'm President of Guastella Associates.

18        Q    Mr. Guastella, did you prepare and cause to be filed

19   12 pages of prefiled direct testimony in this proceeding?

20        A    Yes.

21        Q    All right.  Do you have any corrections or revisions

22   to your testimony?

23        A    Yes.

24        Q    Would you please provide those to the Commission and

25   the parties?

FLORIDA PUBLIC SERVICE COMMISSION

120

1        A    Yes.  I have some typographical errors to correct.

2             On Page 4, Line 6, the word "is" should be "are,"

3   A-R-E.  On the same page, Line 10, the word "increase" should

4   be "incur."  On Page 6, Line 18, the word "great" should be the

5   word "greater."

6             CHAIRMAN CARTER:  Wait a second.  On Line 18?

7             THE WITNESS:  Yes.  The word "great" should be

8   "greater."

9             CHAIRMAN CARTER:  Okay.

10             THE WITNESS:  On Page 7, Line 13, before the word

11   "sections" I would insert "Exhibit JFG-3."  That's Page 7, Line

12   13.  Insert between "and" and "sections" the words "Exhibit

13   JFG-3."  And the last is on Page 8, Line 20.

14             CHAIRMAN CARTER:  State the line again, please.

15             THE WITNESS:  Line 20, Page 8.  The word "it" should

16   be stricken.  It should read, "The calculation would."  That's

17   all I have.

18   BY MR. HOFFMAN:

19        Q    Mr. Guastella, with those corrections, if I asked you

20   the questions that are contained in your prefiled direct

21   testimony today, would your answers be the same?

22        A    Yes.

23             MR. HOFFMAN:  Mr. Chairman, I would ask that

24   Mr. Guastella's prefiled direct testimony be inserted into the

25   record as though read.

FLORIDA PUBLIC SERVICE COMMISSION

121

1             CHAIRMAN CARTER:  The prefiled testimony will be

2   entered into the record as though read.

3             MR. HOFFMAN:  Thank you, Mr. Chairman.

4   BY MR. HOFFMAN:

5        Q    Mr. Guastella, you have attached four exhibits to

6   your prefiled direct testimony.

7        A    Yes.

8             MR. HOFFMAN:  And, Mr. Chairman, those exhibits have

9   been premarked for identification on staff Exhibit 1 as

10   Exhibits 4, 5, 6 and 7.

11             (Exhibits 4, 5, 6 and 7 marked for identification.)

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

134

1   BY MR. HOFFMAN:

2        Q    Mr.  Guastella, have you prepared a summary of your

3   prefiled direct testimony?

4        A    Yes.

5        Q    Would you please provide your summary at this time.

6        A    Yes.  First I guess I would like to just really

7   compliment staff on putting together a proposed rule that takes

8   into account a lot of complex calculations that have been dealt

9   with over the years and I think would effectively reduce a lot

10   of issues and costs associated with used and useful

11   considerations in rate cases.  I know from personal experience

12   not an easy thing to do, and I think they did a commendable

13   job.

14             Another general item, I would like to just point out

15   that as, as you look at used and useful considerations, really

16   the primary goal of rate setting is to cover the cost of

17   providing service.  I guess because I do so much teaching of

18   rate setting I love to go back to the basics, that the rate

19   setting process is covering the cost so that the customers can

20   get the best possible service on a continuous basis, which

21   means you need to serve today's customers today and today's

22   customers tomorrow when customer growth occurs.  So the goal of

23   rate setting is to cover the cost of providing service.  And

24   used and useful is a rate setting term that fits into the

25   overall goal of establishing the cost of providing service to

FLORIDA PUBLIC SERVICE COMMISSION

135

1   the customers.  Used and useful itself is a subpart of the rate

2   setting process.  And I think it's important to keep that in

3   mind because the overriding goal is to make sure utilities have

4   enough revenues and earnings to attract capital to be able to

5   on a continuous basis provide safe and adequate service to

6   customers for growing systems as well as systems that are fully

7   developed.

8             The costs that utilities incur to provide service to

9   customers are based on engineering design criteria so that when

10   systems are designed as new systems and as they are designed

11   for expansion of the systems, the costs the utilities incur are

12   based on those design criteria.  They're not based on used and

13   useful criteria.  So when we examine used and useful in

14   general, we should be looking to what causes the utility to

15   incur the costs and do the used and useful calculations provide

16   that utility with the costs that are necessary to provide

17   service to the customers?

18             The systems were not designed based on used and

19   useful demands or capacities.  The systems were designed based

20   on engineering requirements to make sure that the customers get

21   safe and adequate service.  Used and useful then is a

22   ratemaking term and a ratemaking tool to establish what is an

23   appropriate level of the cost of providing service.

24             I might add that the primary reason used and useful

25   calculations are made in Florida is because of the

FLORIDA PUBLIC SERVICE COMMISSION

136

1   developer-related systems.  So what we want to make sure is

2   that because so many systems are not fully developed, the PSC

3   has correctly over the years established used and useful

4   adjustments in rate proceedings to make sure that the existing

5   customers pay a fair share of the cost of providing service and

6   are not in effect through the rate subsidizing the future cost

7   of providing service.

8             But, nevertheless, the primary goal is what is the

9   cost of providing service to the customers?  And if we depart

10   from the engineering criteria, the reason why the utilities

11   incur cost to provide service because of used and useful

12   calculations, then the used and useful calculations are going

13   beyond what they should be going through.

14             With that in mind, in my review of staff's proposal I

15   really only had a small handful of items that I would suggest

16   may focus the rule in on a more proper determination of the

17   cost of providing service.

18             One of the issues I raise is the use of the maximum

19   day.  The proposed rule has a maximum day in the test year,

20   wording to the effect that you use a maximum day for the test

21   year.  Systems are not designed based on a rate setting test

22   year.  Engineers don't know when there's going to be a rate

23   case or a rate setting test year.  When they design systems,

24   they design systems to meet the maximum day.  And if you look

25   at engineering criteria or DEP criteria, they do not refer to a

FLORIDA PUBLIC SERVICE COMMISSION

137

1   rate setting test year.  They refer to the maximum day.

2             I think the PSC would want the utilities to design

3   the system to meet the demands of the customers on the maximum

4   day, whether that's during the test year or before the test

5   year.  Or if it's a projected test year, what the maximum day

6   is going to be for a projected test year.  If you don't, you're

7   not giving the utility enough money to meet the demands of the

8   customers that actually occur, whether it's before, during or

9   after the test year.  So one of my recommendations is to

10   eliminate the wording that limits the maximum day to the test

11   year.  It's not based on the design criteria and, therefore,

12   more importantly, it's not based on the criteria that requires

13   the utility to spend money for a utility system that's designed

14   to serve the customers.

15             The other adjustment I would make is -- oh, I just

16   would note that the maximum day used for design purposes,

17   whether it's designing a new system or whether it's expansion

18   of an existing system to serve more and additional customers

19   and additional demands, engineers always build in what I call a

20   cushion or a factor of safety into the design criteria.  I

21   don't know of any instance that I've examined where the goal of

22   the design was to establish exactly what the customers were

23   going to use in actuality once the system is built and the

24   customers are connected.  There is always a cushion over and

25   above what's actually going to be used.  Otherwise, you're

FLORIDA PUBLIC SERVICE COMMISSION

138

1   always right at the brink of meeting or not meeting the maximum

2   day demands.  So all design criteria and I believe DEP design

3   criteria want the maximum day design to be something greater

4   than what's actually going to be experienced, and I think it's

5   just logical and makes common sense.  You want to have a system

6   that after it's built is going to have some additional capacity

7   built into it beyond what the actual demands of the customers

8   turn out to be.  And I think that's -- and I know that's the

9   way systems are designed.  And I think the used and useful

10   rules do not base the allowance on the design maximum day but

11   on an actual maximum day.  To that extent the used and useful

12   rules are conservative.

13             I'm not recommending that you change the used and

14   useful rules, but I am recommending that when I get into a

15   couple of the other areas, we keep that in mind, that there is

16   a level of conservative allowances of cost built into the rules

17   because we're dealing with ratios of actual maximum demands in

18   relation to capacity.  And there is a factor of conservatism

19   built into the used and useful rule that's not allowing what

20   the cost to design the system was when it was designed.

21             One of those is unaccounted for water.  Unaccounted

22   for water does not change the cost the utility incurred to

23   build and design the system.  All systems have unaccounted for

24   water.  All systems are designed and engineers anticipate that

25   certainly there's going to be unaccounted for water.  I'm not

FLORIDA PUBLIC SERVICE COMMISSION

139

1   aware of any water system that does not have unaccounted for

2   water.  The question of unaccounted for water is, in fact, an

3   economic question.  As systems age and the unaccounted for

4   water increases, the issue then becomes if it becomes

5   excessive -- and it's not so significant to me whether staff

6   uses a 10 percent or some other percentage, so the 10 percent I

7   don't argue with.  But if anything greater than 10 percent is

8   going to be considered excessive unaccounted for water, then

9   for the rate setting process on the operating expenses

10   adjustments are made for power and chemicals because the

11   unaccounted for water exceeds 10 percent.

12             However, if the Commission finds that the unaccounted

13   for water is excessive, then they should do one of two things.

14   Do an economic test.  If the unaccounted for water that's in

15   excess should be reduced, provide the funds to the utility

16   that's cost-effective to reduce the unaccounted for water.  If

17   it's not cost-effective to reduce, say, a 12 percent

18   unaccounted for water or a 13 percent unaccounted for water

19   down to 10 percent, then don't make an adjustment.  But in

20   either case, the unaccounted for water does not affect the

21   money that the utility had to spend to design the plant.  So I

22   think adjusting the used and useful calculation for unaccounted

23   for water percentages violates in my mind the cost principle

24   that the utility had to incur the cost to serve the customers.

25   As systems age and unaccounted for water becomes greater and

FLORIDA PUBLIC SERVICE COMMISSION

140

1   greater, the cost the utility incurred to make an investment in

2   that plant does not change, does not get reduced and should not

3   be reduced.

4             If you will picture that the entire cost of the plant

5   was borrowed and the utility continues to pay principal and

6   interest on the borrowed money for a plant that was

7   well-designed to meet the needs of the customers but over time,

8   like all water systems, the unaccounted for water increases to

9   the point where it either should or should not be reduced, I

10   think then the Commission should act more directly.  If the

11   unaccounted for water should be reduced, direct the company to

12   reduce it and provide the money to do that.  If that's not

13   cost-effective, then don't make an adjustment.  But I don't

14   think take away -- I don't think it's reasonable to take away

15   an investment the utility made that does not reduce because of

16   unaccounted for water.

17             The other issue I raised was with respect to high

18   service pumps, and this is the last one.  As I said, I had

19   really very few disagreements with staff's proposal.  And I do

20   agree that the high service pumps could be treated as a

21   separate item.  I depart a little bit from what I believe is

22   staff's intent.

23             It's been my experience that most systems, the high

24   service pump cost is a very small part of the total cost of

25   utility plant in service.  So I agree with staff that this is a

FLORIDA PUBLIC SERVICE COMMISSION

141

1   very small item in terms of total cost.  I also believe that

2   most systems -- and I make a distinction between wells that

3   service high service pumps compared with systems that have

4   separate high service pumps apart from the wells.  I think if

5   you have high service pumps in the context of this rule, you're

6   talking about pumping facilities that are not source of supply

7   facilities.  You're talking about the wells, and the rules

8   provide for used and useful calculation for the sources of

9   supply of the wells.

10             A separate issue, therefore, is high service pumps

11   where the high service pumps are separate and distinct from the

12   well pumps.  Those high service pumps don't happen that often

13   in most small systems.  I was involved in the Aqua Florida

14   cases, and out of the 56 utilities, only 14 of them had

15   separate high service pumps.  And of those I treated them all

16   as 100 percent used and useful for a number of reasons which I

17   don't need to get into here.  But I think staff is correct, the

18   high service pumps are a very small part of the costs.  I don't

19   think there's a separate rule that's necessary.  And I do think

20   it's a complex item to include in a formula for determining

21   high service pumps.

22             CHAIRMAN CARTER:  Thank you very kindly.

23             MR. HOFFMAN:  Does that conclude your summary,

24   Mr. Guastella?

25             THE WITNESS:  It does.

FLORIDA PUBLIC SERVICE COMMISSION

142

1             MR. HOFFMAN:  And Aqua would tender Mr. Guastella for

2   cross-examination.

3             CHAIRMAN CARTER:  Mr. Reilly, you're recognized.

4                          CROSS EXAMINATION

5   BY MR. REILLY:

6        Q    Does unaccounted for water, Mr. Guastella, does it

7   benefit customers?

8        A    I'm sorry.  Does it what?

9        Q    Does unaccounted for water benefit customers?

10        A    No.

11        Q    Okay.  Do customers have any control over unaccounted

12   for water?

13        A    No.

14        Q    What regulatory body, changing subjects, governs fire

15   flow requirements for water systems?

16        A    I'm not aware of any regulatory body in terms of a

17   utility regulatory body.  The, the fire flow requirements are

18   designed based on criteria that the engineers are going to look

19   to, and local government will have criteria.  But there are

20   also criteria that engineers would follow that go beyond local

21   government such as ISO and, and other criteria for meeting

22   potential fire demands within any system that's being designed.

23        Q    But is it not true that any system that's built must

24   at least meet the fire flow requirement of the respective

25   jurisdiction that they're building the system in?

FLORIDA PUBLIC SERVICE COMMISSION

143

1        A    Yes.  And I think you said "at least."  And that's

2   really why I have included language that says let's use the

3   most reasonable fire flow requirement.  Because the local

4   government may show a minimum fire flow requirement that's not

5   necessarily the fire flow requirement that a system should be

6   designed to meet.  And I see that it's just as easy in a rule

7   to say meet the most reasonable fire flow requirement as well

8   as then providing that of local government or a minimum of

9   500 gallons per minute.  I think it's important to note that

10   fire flow requirements may very well exceed what the specific

11   language in local government codes may require.

12        Q    Does the Florida Department of Environmental

13   Protection have any specific fire flow requirements for water

14   utilities?

15        A    I think they, I think they refer to the National Fire

16   Protection Association and various other standards.  I don't

17   know if they've promulgated their own.

18        Q    But you don't know if FDEP has any requirements for

19   fire flow per se?

20        A    That's right.

21        Q    Does the ISO, the Insurance Service Organization,

22   issue any permits to construct or operate water utilities?

23        A    No, not to my knowledge.

24        Q    Is a water utility in violation of the provisions of

25   DEP's rules if it does not follow ISO standards?

FLORIDA PUBLIC SERVICE COMMISSION

144

1        A    If a water utility is designed and does not meet a

2   fire flow requirement that's appropriate based on the standards

3   that ISO has promulgated, then I think it could be in

4   violation.  I think DEP requires utilities to meet a required

5   fire flow and an appropriate fire flow.  And if it does not do

6   that, I think it could very well be contrary to standards that

7   ISO has developed.

8        Q    But you're not aware of any specific provision of

9   FDEP rules that requires the following of ISO standards?

10        A    It doesn't specifically state ISO.  But if ISO

11   standards are not met and the utility is not capable of

12   providing the needed fire flow requirement, then that's a

13   violation of a fire flow requirement that the utility should be

14   designed to meet.

15        Q    You're recommending a fire flow allowance based upon

16   NBFU, the National Board of Fire Underwriters, and ISO, the

17   Insurance Service Organization, which provides fire flow for

18   multiple hydrants need to meet fire flow demands at every

19   location throughout the system and to meet coincidental,

20   coincident fires; is that correct?

21        A    Only if the systems, only if you analyze the systems

22   where such considerations are needed.  I'm not saying that

23   every system should have a fire flow requirement for multiple

24   or coincidental fires, but I certainly think every system

25   should be analyzed based on the construction of the buildings

FLORIDA PUBLIC SERVICE COMMISSION

145

1   that are going to require fire protection.  And if the formula

2   for fire flows show that buildings of sufficient square footage

3   and fire requirements require something greater than the

4   minimum in a local government code, that that system should be

5   designed to meet the greater level, whether it's 1,000 gallons

6   per minute, 2,000, 3,000 or 4,000 gallons per minute.  At some

7   point you do reach a judgment as to whether or not a large

8   system would have to have the capability of meeting

9   coincidental fire demands, and at that point you would take

10   also into account the potential of multiple fires.

11        Q    But I understood your recommendation was that you did

12   not support the, at least the current draft of the proposed

13   rule that said that you would meet either the minimum of the

14   fire flow required by the local government or this default

15   amount, which is two hours at 500 gallons a minute.  In lieu

16   thereof you wanted to substitute these requirements and all of

17   these additional --

18        A    No, that's not correct.

19        Q    Okay.

20        A    My testimony says that, insert the words "in addition

21   to meeting local fire flow requirements and the minimum of 500

22   gallons per minute," insert the words "a reasonable fire flow."

23        Q    And your definition of reasonable fire flow includes,

24   as I understand it, the need to meet demands at every location

25   throughout the system to meet coincident fires and to provide a

FLORIDA PUBLIC SERVICE COMMISSION

146

1   fire flow for multiple hydrants; is that correct?

2        A    No.  I did not provide a definition within the rule.

3   I just said when you take a look at any water system, what fire

4   flow requirements should that water system meet?  And if you

5   take a look at a system that has commercial properties or

6   multistory properties, determine the fire flow based on

7   whatever engineering criteria, and the engineering criteria and

8   standards are readily found in ISO publications to meet those

9   fire flow requirements.

10             I don't think it should be excluded from a rule that

11   a reasonable fire flow requirement should not be included as

12   part of a rule for used and useful.

13        Q    So you believe any rule that's adopted has to give

14   the utility the opportunity to establish what they think is a

15   reasonable fire flow requirement that exceeds the local

16   governmental requirement or this two hours at 500 gallons per

17   minute?

18        A    If it exceeds it.  It may not in all cases because

19   many of the local governments refer to standards that are

20   similar to what ISO has.  But if there's a minimum standard in

21   local government but they also refer to other standards such as

22   ISO or the National Fire Protection Association, then analyze

23   the system based on how it was designed to meet those fire

24   demands.

25             I think the cost that you give a utility in rates

FLORIDA PUBLIC SERVICE COMMISSION

147

1   should enable it to meet the fire demands, fire flow

2   requirements that the fires would demand.  And if systems are

3   designed on that basis, that's part of what would be presented

4   as part of the used and useful analysis:  A fire flow that's

5   actually needed for a particular system.

6        Q    Have you recommended this additional fire flow

7   potential allowance in other cases that you've testified in

8   Florida?

9        A    I believe I have.

10        Q    And what case would that be or cases?

11        A    I think in most all of them.  I can't remember all of

12   them.  There have been a number of cases I've testified in

13   Florida, and the fire flow requirements that I used were based

14   on what I believe the system should have been designed to meet

15   and incurred costs to meet.

16        Q    Have any other -- has the Florida Public Service

17   Commission or any other local governing utility board ever

18   accepted your recommendation for any one of these, the meeting

19   the fire flow demands at every location or coincident fires or

20   multiple hydrants?  Do you have cases in Florida where that's

21   been accepted?

22        A    I don't know if the cases in Florida -- I believe

23   there were.  I believe we dealt with this issue maybe in a

24   Deltona case where there was a need for considering storage

25   facilities and multiple fires.  I don't know all of the -- I

FLORIDA PUBLIC SERVICE COMMISSION

148

1   don't recall all of the cases I testified in Florida where I

2   recommended a fire flow requirement where that fire flow

3   requirement was or was not used.

4        Q    But you have no --

5        A    I just don't remember the data.

6        Q    You have no cases today to indicate, that would

7   support this, this additional level of fire flow that you can

8   offer us today, Florida cases that support that, that testimony

9   or that recommendation?

10        A    Well, let me put it in a different way.  I don't know

11   of any case where the Florida Commission said the fire flow

12   requirement is reasonable but we're going to only use a minimum

13   for local government instead of what's a reasonable fire flow.

14   And I think having a rule that simply says a reasonable fire

15   flow is an appropriate used and useful rule to have.

16        Q    Did you testify in a St. Johns County Regulatory

17   Authority case?

18        A    For Intercoastal Utilities?

19        Q    Intercoastal Utilities.

20        A    Yes.

21        Q    And that would be Docket Number 04007-0011-001,

22   subject to check?

23        A    I don't know the number.

24        Q    Well, that would be an '04 case?

25        A    That was before St. Johns County, not the Florida

FLORIDA PUBLIC SERVICE COMMISSION

149

1   Public Service Commission.

2        Q    That was before the St. Johns Regulatory Authority?

3        A    Yes.

4        Q    And my question to you is in that case did not the

5   hearing officer and ultimately the St. Johns County Board of

6   County Commissioners approve in his recommended order -- did

7   not agree with you in your fire flow recommendation?

8        A    I believe that's correct.  I believe I, I made

9   calculations of what the fire flow requirement would be for the

10   structures for the Intercoastal Utility, and there were

11   structures of private homes that, believe it or not, had square

12   footage of 18,000 square feet, there were commercial buildings

13   that had square footage of greater than that.  I calculated a

14   fire flow, I believe, of 3,000 gallons per minute or possibly

15   3,500 gallons per minute.  I don't remember which.

16             I think, I think the administrative, the judge that

17   was assigned to that used a 1,500 gallons per minute.  And I

18   would hope that the Florida Public Service Commission wouldn't

19   make the same kind of mistake.  Because I would think that if

20   you're going to fight fires that require 3,000 gallons per

21   minute, you would want the utility to do that, not allow

22   something that was less.

23        Q    But in that case they did not -- the St. Johns County

24   Authority did not accept the fire flow requirement for multiple

25   hydrants meeting coincident fires; is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

150

1        A    I don't believe I asked for recommended multiple fire

2   flows.  I believe I recognized that a fire demand should be

3   3,500 gallons per minute.

4             MR. REILLY:  No further questions.

5             CHAIRMAN CARTER:  Mr. Friedman.

6             MR. FRIEDMAN:  Yes.  Thank you.

7                          CROSS EXAMINATION

8   BY MR. FRIEDMAN:

9        Q    Mr. Guastella, do you agree with Mr. Woodcock's

10   belief as espoused in his prefiled testimony that if actual

11   demand is less than design demand, that the risk should be

12   placed on the utility?

13        A    No.  The utility has a requirement of meeting the

14   demands of the customers and building facilities to be sure to

15   do that.  The utilities spend money based on the design

16   criteria that will enable the utility to meet demands on the

17   system, knowing that the actual demands are going to be less

18   than what the design is.  And as I indicated in my opening

19   remarks, the costs utilities incur are based on the design of

20   the system and, and rate setting doesn't spread any risk to

21   customers.  The utilities have to cover the cost of providing

22   service, and rate setting is a process in which the cost of

23   providing service is the goal.  And the cost of providing

24   service is based on the design criteria, not the actual demands

25   on the system.

FLORIDA PUBLIC SERVICE COMMISSION

151

1             MR. FRIEDMAN:  That's all I have.

2             CHAIRMAN CARTER:  Commissioners?  Mr. Reilly.

3             MR. REILLY:  We will let that question -- I think we

4   were checking and it appears that that is a quote out of his

5   rebuttal testimony.  It might be more appropriately asked at

6   that time.  However, he's asked the question, he's gotten the

7   answer, and I really will let it go at that.  But it's my

8   understanding that, that it was actually a question concerning

9   his rebuttal testimony, which, of course, will be more

10   appropriately done at a later time.

11             MR. FRIEDMAN:  I'll ask it again later.

12             CHAIRMAN CARTER:  Okay.  Commissioners?

13             Okay.  Staff.

14             MR. JAEGER:  I'll be spelling Ms. Gervasi for this

15   one.

16             CHAIRMAN CARTER:  You're recognized.

17                          CROSS EXAMINATION

18   BY MR. JAEGER:

19        Q    Ralph Jaeger for Commission staff.  I think

20   Mr. Reilly was all around it, but I'm talking about fire flow

21   first, and he was talking about, you know, multiple meters,

22   multiple fires.  And I think it's on page -- could you turn to

23   Page 7, Lines 2 through 4?  And it says there, "I would simply

24   change the last phrase to read, 'where fire flow is provided,

25   an appropriate fire flow'" -- you used reasonable but you're

FLORIDA PUBLIC SERVICE COMMISSION

152

1   actually saying appropriate fire flow?

2        A    Yes.

3        Q    And for appropriate fire flow are you referring to

4   the Insurance Service Organization and its predecessor, the

5   National Board of Fire Underwriters?

6        A    Those are two sources that I think you could, you

7   could apply formulas to determine what the appropriate fire

8   flow is.

9             You could also find it through the, the National Fire

10   Protection Association would also provide formulas for

11   determining appropriate fire flows.  So basically what I'm

12   saying is do not limit the rule to a minimum standard.  I think

13   an appropriate fire flow is appropriate to use in a rule.

14        Q    Well, isn't this rule sort of like a default type

15   rule?  I mean, we start out here and doesn't it give adequate

16   where you can provide justification for greater?

17        A    Yes.  And I believe as a default using an appropriate

18   fire flow is, is a good default.

19        Q    Okay.  And I believe you talked about the St. Johns

20   County.  Has this Commission ever used ISO or NBFU guides and

21   formulas for calculating fire flow requirements?

22        A    As I said before, I can't remember all of the fire

23   flows that I've used in the various used and useful

24   calculations that I've made in Florida.  But I seem to recall

25   that many of the times what I recommended was accepted and that

FLORIDA PUBLIC SERVICE COMMISSION

153

1   was my source of determining fire flow requirements.  I use, I

2   use the ISO as a standard and its predecessor all over the

3   country, and all over the country I rarely get objections to

4   what those fire flows are.  Because when those same standards

5   and formulas are applied to utilities, they come up with a

6   pretty reasonable level of fire flow requirement.  So I can't

7   say the Commission has not because if they've accepted any of

8   my proposals, that's what it was based on.

9        Q    As a general rule do you know if these NBFU or ISO

10   guides conflict or coincide with the local county government

11   fire requirements?

12        A    Well, the local, local government, and I don't know

13   them all, but some of them that I've looked at, they actually

14   refer to those standards or similar standards.  So if we're

15   referring in the rule to local government and local government

16   in turn is referring to standards or formulas, then in effect

17   by referring to local government you are asking for a fire flow

18   requirement based on those very standards.  You're just going

19   through a more circuitous route doing it through reference to

20   the local government rather than just saying "an appropriate

21   fire flow requirement."

22        Q    Well, do most Florida counties have an ordinance or

23   rule on the required fire flow for their particular county?

24        A    Well, the ones I've looked at have a minimum or use

25   the National Board of Fire Protection or some ISO standard.  So

FLORIDA PUBLIC SERVICE COMMISSION

154

1   they say to the utilities, build a system to meet ISO standards

2   or National Board of -- National Fire Protection Association

3   standards.  So you're really -- the government is telling the

4   utility to use the standards that I'm referring to.  And if the

5   utility is using those standards, then the rule says that's

6   fine.  I'm simply saying use an appropriate required fire flow.

7   And if that source is the same, is referencing the same

8   standards that the local government is referencing, then fine.

9   I think the real important point is you want the utilities to

10   meet the appropriate fire flow requirement and you want to give

11   them the money to do that.

12        Q    Okay.  Moving on, the next questions are about

13   unaccounted for water.  Could you turn to Page 5 of your

14   testimony?

15        A    I have it.

16        Q    Okay.  On Line 6 through 8 you state, "I do not

17   believe it is appropriate to make adjustments to demands for

18   unaccounted for water because eventually all systems experience

19   increasing levels of unaccounted for water as the systems age."

20   Is that correct?

21        A    Yes.

22        Q    What responsibility does the utility have to control

23   the amount of unaccounted for water?

24        A    Well, they have -- really the entire burden is on the

25   utility to make sure that its unaccounted for water does not

FLORIDA PUBLIC SERVICE COMMISSION

155

1   grow to the point where it's economical to undertake the

2   studies and repairs to correct the unaccounted for water.  I

3   think it's inevitable that all systems, at least it's been my

4   experience that all systems experience unaccounted for water

5   most of the time since the day they were installed.  There's

6   always some level of unaccounted for water.

7             And as the systems age different systems are going to

8   experience more and more unaccounted for water.  At some point

9   the utility should, and it's their responsibility, should

10   analyze their unaccounted for water and decide whether or not

11   it's worth spending the money, getting rate relief for the

12   money they spend and reducing the unaccounted for water, or the

13   unaccounted for water simply hasn't grown to the point where

14   it's cost-effective to do that.

15             In turn, that information should be provided by the

16   utility to the Commission.  And the Commission should then make

17   a decision, do they allow the utility the money to correct the

18   problem or is it not cost-effective at this time, and you wait

19   until it becomes cost-effective?  If the utility doesn't live

20   up to that responsibility, then I know staff will take that

21   role as a regulator and tell the utility we find through our

22   examination that it's cost-effective to, to reduce your

23   unaccounted for water, so do so.  And what it does is it

24   reduces power and chemicals, basically the variable costs of

25   providing water.  There is an added cost to undertake the

FLORIDA PUBLIC SERVICE COMMISSION

156

1   studies to reduce the unaccounted for water.  But what does not

2   happen is the cost of the assets do not change.  And

3   unaccounted for water, and I agree with staff, it's really a

4   very small part of the total water and a very small part of a

5   maximum day demand, if any.  So it's just not an appropriate

6   adjustment to make to the cost of the assets, which were the

7   minimum cost that's being allowed to the utility to recover.

8             I think the appropriate regulatory response is if

9   unaccounted for water is causing, one, a problem with

10   conservation or, two, the cost for variable costs for power and

11   chemicals should be reduced because it's more cost-effective to

12   do that, then I think the Commission and the staff should

13   essentially take the bull by the horns and say fix it because

14   it's cost-effective to do it or don't fix it.  But don't reduce

15   an investment that had to be made in order to provide service

16   to the customers.  So I just don't think it belongs in a used

17   and useful calculation for the cost of utility plant

18   facilities.

19        Q    I think staff in this rule is recommending a

20   10 percent default.  What happens if unaccounted for water

21   approaches, say, 30 percent, would you still say don't reduce

22   the --

23        A    I think my answer would be the same.  I think then if

24   it's cost-effective to spend the money to reduce the 30 percent

25   down to 10, then include the cost in the rates, have the

FLORIDA PUBLIC SERVICE COMMISSION

157

1   utility reduce the 30 percent down to 10, and the cost of the

2   utility system is not going to -- the cost of the assets

3   themselves, the physical plant is not going to change.  But you

4   then solve the problem of unaccounted for water directly and

5   that's my testimony.  Solve it directly by saying it's too

6   high, reduce it, and here's the money to reduce it, and then

7   make whatever adjustments during the test year for ratemaking

8   purposes to power and chemicals.  But since you're going to

9   reduce it down to the level it should be at, there's no need to

10   make and it's improper to make an adjustment to the cost of the

11   assets which really did not change because of unaccounted for

12   water.

13             CHAIRMAN CARTER:  Mr. Jaeger, could you hang on for

14   one second, please?

15             Commissioner McMurrian, you're recognized.

16             COMMISSIONER McMURRIAN:  Thank you, Chairman.

17             Mr. Guastella, following up on this line of

18   questioning about your comment about taking the bull by the

19   horns if it's, if it's cost-effective anyway and basically

20   having the Commission tell the utility to do it if it's

21   cost-effective, I guess, I guess this gets into philosophy a

22   little bit.  But do you really think the Commission needs to

23   direct the utility to do it if it's the most cost-effective

24   approach anyway or should the utility be taking the bull by the

25   horns itself and do it and then come to the Commission and say

FLORIDA PUBLIC SERVICE COMMISSION

158

1   we felt like this was the most cost-effective way to do it and

2   now we seek recovery because that was the most appropriate way

3   to do it?

4             THE WITNESS:  I agree with you 100 percent.  I think

5   the utility should take the bull by the horns and monitor its

6   lost and unaccounted for water.  Obviously you have some

7   utilities and they're small utilities and they're managed to

8   the extent of what a small utility has in terms of staff and

9   engineering staff, and many of them don't have engineering

10   staff.  So I think, you know, the reality is the larger

11   utilities you have that have staff and engineering staff, they

12   monitor these things better than the smaller utilities that do

13   not have in-house staff.  And they don't see without separate

14   studies the cost for power and chemicals being so significant

15   because of such factors as unaccounted for water.  And it's a

16   tough issue because sometimes solving the unaccounted for water

17   problem is so much more costly than just accepting power and

18   chemical costs that it may very well be that it's not

19   cost-effective to do that.  But I think all responsibility

20   first lies with the utilities.  And then the utilities are

21   regulated by Commissions because if they don't live up to that

22   responsibility, then the second layer of protection for the

23   customers is the PSC, the regulatory agency.  You know, it's a

24   costing and ratemaking issue that if the utility doesn't do

25   what it should be doing, then the, the Commission can.

FLORIDA PUBLIC SERVICE COMMISSION

159

1             But I don't think the used and useful and the cost of

2   the assets is really affected by the decision whether it's at

3   the utility level for unaccounted for water or at the PSC level

4   for unaccounted for water.  In both cases it has to do with

5   reducing costs for one of two purposes:  Conservation, which

6   may override any cost principles, or the cost-benefit analysis

7   that says power and chemicals are growing to the point where

8   it's getting so costly to deal with unaccounted for water that

9   let's spend the money to correct the problem.  In neither case

10   did the cost of the assets change because they were designed

11   based on design criteria that's greater than what actual

12   demands on the system are, and I think the unaccounted for

13   adjustment is not an appropriate adjustment in the used and

14   useful calculation.

15             COMMISSIONER McMURRIAN:  I have one follow-up,

16   Chairman.  Thank you.

17             Mr. Guastella, do you see the proposed rule as an

18   incentive, and maybe I should say it's more, perhaps more of a

19   stick incentive than a carrot incentive, but for the utility

20   to, you know, take the right approach with respect to the

21   excessive unaccounted for water?

22             THE WITNESS:  I think the incentive is when the

23   Commission makes an adjustment for power and chemicals, and I

24   think, you know, the Commission then is telling the company

25   we're not allowing you these operating expenses because if you

FLORIDA PUBLIC SERVICE COMMISSION

160

1   corrected the problem, you wouldn't have these operating

2   expenses.  And I'm assuming, however, that the staff of the

3   Commission and the Commission may at some point recognize that

4   it's better to have some extra chemicals and power costs than

5   to spend so much money to correct a problem that sometimes is

6   very difficult to locate, detect and then repair a distribution

7   system, for example.

8             So it's, it's a, it's a difficult problem to solve,

9   it's a hard problem to make a judgment on on a cost-benefit

10   analysis, but I don't think the message comes through used and

11   useful.  I think the Commission's measure should be design your

12   system to serve the customers.  And then if you have a problem

13   like unaccounted for water, to me it's the same kind of problem

14   where you're incurring expenses we don't want the customers to

15   pay for but you're not incurring a cost of plant that you don't

16   want the customers to pay for.  The cost of the plant isn't

17   affected by the unaccounted for water.  So give the message to

18   the utilities that the costs that affect the customers,

19   variable costs for power and chemicals, is what we're going to

20   be concerned with.  We're not going to take away a cost of

21   plant that was necessary for you to serve the customers.  It's

22   just not the appropriate place to make that adjustment.

23             CHAIRMAN CARTER:  Thank you.

24             Commissioner Skop.

25             COMMISSIONER SKOP:  Thank you, Mr. Chair.  Just a

FLORIDA PUBLIC SERVICE COMMISSION

161

1   follow-up to Commissioner McMurrian's and Mr. Jaeger's

2   question.

3             With respect to the staff proposed limitation for

4   unaccounted for water, doesn't that serve somewhat as a

5   deterrent function to the extent that it would preclude

6   complacency in not fixing small problems before they grow into

7   bigger ones?  I mean, if you could chase down smaller leaks

8   just as part of normal operation and maintenance.  Because I

9   think that Mr. Jaeger's question goes to the heart of probably

10   staff's concern.  If we allow that to go unchecked, at what

11   point, you know, will the small problems not get fixed before

12   they perhaps grow into larger problems, which I think you

13   stated that the regulators should provide the cost benefit for

14   fixing.

15             THE WITNESS:  Well, I guess, you know, having been a

16   regulator, I'm trying to put myself in your shoes.  And if I

17   put myself in the shoes of a regulator again, I'm conflicted by

18   the fact that you would deny the utility some money because you

19   want to send them the message to fix leaks.  But if they said

20   it's going to cost more money to fix the leak than the costs

21   we're incurring for power and chemicals, you wouldn't direct

22   them to fix the leak.  See, I'd rather as a regulator say

23   that's a problem that's worth fixing so fix it.  I don't think

24   it's sending a message if you say we're going to penalize you

25   for having lost and unaccounted for water, but it's not such a

FLORIDA PUBLIC SERVICE COMMISSION

162

1   big lost and unaccounted for, so we're not going to tell you to

2   fix the problem.  And I think that's the problem when you're

3   mixing what should be used and useful for assets and what

4   should be a decision for operating expenses.

5             Unaccounted for water is really an operating expense

6   problem.  And if you're not going to tell the utility to fix

7   the operating expense problem because you don't think it's

8   worth it, I don't see how you can at the same time say but

9   we're going to send you a signal that we're going to penalize

10   you for an operating expense problem that we're not going to

11   tell you to fix because it's not worth fixing.  You've got a

12   conflict there.  And I think, I think you're sending the wrong

13   message to the utility.  We're going to make, we're going to

14   penalize you for something we wouldn't direct you to fix

15   because we don't think it's worth fixing.  So let's leave the

16   problem alone, don't fix it, but we're going to take some money

17   away from you as an incentive to fix it.

18             I don't know if you see the same conflict I see, but

19   that's the conflict I see.  You're penalizing for something

20   that you wouldn't direct them to fix because you don't think

21   it's worth fixing, and I think that's why this doesn't belong

22   in the used and useful calculation for assets.

23             COMMISSIONER SKOP:  Thank you for that alternate

24   viewpoint and perspective.  I appreciate that.

25             THE WITNESS:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

163

1             CHAIRMAN CARTER:  Commissioners, any further?

2             Mr. Jaeger, you're recognized.

3   BY MR. JAEGER:

4        Q    I had just one last question on this line of

5   questioning.  Say you're at maximum capacity and you've got

6   40 percent unaccounted for water and it's still a growing

7   utility.  Now if they were not doing, if they didn't have the

8   excessive unaccounted for water, if they didn't have such a

9   high amount, they wouldn't have to buy new plant.  So that

10   investment, they would have to put in a new plant, would that

11   change your testimony here today when it's already at maximum

12   and it's a high percentage of unaccounted for water?

13        A    You know, in the real world I don't think that would

14   happen because if they got to be close to the maximum and they

15   had growth to go, DEP won't let them get there.  Because if

16   they're reaching 75 percent of their capacity, DEP is going to

17   tell them start reporting so that you start expanding the

18   capacity.  And then as your demands start to exceed the

19   75 percent, you're already planning for the expansion of the

20   system and DEP requires you to do that.

21             So the system really should never get from an

22   engineering perspective to be 40 percent if it's already at

23   demand.  First of all, it should never get to demand.  If

24   they're growing and the demand is going to be greater than what

25   they're reaching, they'll never get there because DEP won't let

FLORIDA PUBLIC SERVICE COMMISSION

164

1   their system exceed 75 percent of the maximum day requirement

2   that's anticipated over the next five to ten years.  So your

3   hypothetical really should never and could never happen in a

4   reasonable world of utilities trying to provide service and DEP

5   monitoring what the demands on the system are and what the

6   capacities of the system are.  So you're asking me for an

7   extreme that really should never happen.

8        Q    Going to the next line of questioning, the maximum

9   day demand versus the maximum five-day average, could you turn

10   to Page 4, Lines 17 through 19?

11        A    Yes, I have it.

12        Q    You say, "I recommend eliminating the provision to

13   use a maximum five-day average, and instead use the next

14   maximum day demand that had no unusual occurrence."  Would that

15   be true no matter how many unusual occurrences you had?  Say

16   you had four or five days unusual occurrences.  You would just

17   keep going down until you hit the first maximum day without an

18   unusual occurrence?

19        A    Yes.  I'd go find the maximum day demand on the

20   system.  And, incidentally, whether it's during or prior to or

21   after the test year, I'd go find the maximum day demand on the

22   system because, number one, it's an actual demand which is

23   conservative in lieu of the design demand, but certainly every

24   engineering criteria, DEP says we want the maximum day, we

25   don't want an average.  We want you to exclude from the maximum

FLORIDA PUBLIC SERVICE COMMISSION

165

1   day any unusual occurrence.  So find the maximum day that

2   didn't have something unusual and use it.

3        Q    To your knowledge has the Commission ever used the

4   next maximum day after throwing out one or more days with an

5   unusual occurrence?

6        A    I don't know.

7        Q    Could you turn to Page 8, please.  On Page 8 of your

8   testimony, Lines 11 through 14, you state, "Typically, high

9   service pumps connect to a common transmission main, and when

10   two or more pumps are operated at the same time, they pump

11   against pressure, resulting in flow rates that are less than

12   their respective rated capacity."  Is that correct?

13        A    Yes.

14        Q    Can you give us an example of a PSC-regulated water

15   system or another system that has that situation?

16        A    The one I can recall that I assume, at least it was

17   before the PSC was Marco Island.  Marco Island had raw water

18   pumps, high service pumps that brought raw water down to the

19   treatment plant.  The high service pumps and the raw water

20   supply were on the mainland pumping the water to a treatment

21   plant that was on Marco Island.  And those pumps had rated

22   capacities individually, but when they were operated together

23   the capacity to deliver the water to the system was much less.

24             I believe the Commission accepted that the effective

25   capacity of the pumps running together was the capacity to use

FLORIDA PUBLIC SERVICE COMMISSION

166

1   in the used and useful analysis.  That's one of them I can

2   remember.  You know, I don't know if I can remember others off

3   the top of my head, but I know there have been others as well.

4        Q    When two or more high service pumps run

5   simultaneously how difficult is it to calculate the percentage

6   of reduction?

7        A    It needs to be calculated.  And maybe what you need

8   to do is flow the pumps together to see what's happening.

9   Because I think if you have two pumps, and let's assume they've

10   got a rated capacity individually of 1,000 gallons per minute

11   but when you run them together it's 900 gallons per minute

12   because they're pumping against the head, the rated capacity,

13   it's been my experience in the cases where I've had multiple

14   high service pumps that the rated capacity is on an individual

15   basis.  And you would then use the lower capacity system if

16   they were operated together.  And if you had three 1,000 gallon

17   per minute pumps and they were operated together, then the

18   demand on the system might go from 900 each down to 800 each.

19             So I don't think the pumps are rated based on what is

20   the range of flow when one, two or three pumps are operated

21   individually?  I think what happens is you can only look at the

22   rated capacity of each pump and then know that it's going to be

23   something less if two are operated and something even less if

24   three are operated together.  So it becomes a bit of a complex

25   problem.  One of the reasons in addition to it's rare and in

FLORIDA PUBLIC SERVICE COMMISSION

167

1   addition to it's a very minor cost in relation to total, that

2   I'd agree that the high service pumps shouldn't be pulled out

3   and treated as a separate piece of the rule.

4        Q    Are you familiar with jockey pumps?

5        A    Tell me about jockey pumps.

6        Q    I'm just asking are you familiar with them?

7        A    You mean where they'll alternate the use of various

8   pumps, high service pumps?

9        Q    Can you describe what you consider a jockey pump, see

10   if we're --

11        A    Well, to me that would be where you have pumps that

12   might be used where they're mobile, you could apply them at

13   different locations, or if you have alternate uses of, of pumps

14   that are available at the plant itself.

15        Q    But they're usually smaller and maybe more mobile?

16        A    Yes.

17        Q    And can they pump against the pressure of the larger

18   high service pumps?

19        A    It depends on the configuration of the piping.

20        Q    Would you include the jockey pumps in the used and

21   useful calculation?

22        A    I'd have to take a look at all the pumps and see how

23   and when they're used.  I couldn't tell you off the top of my

24   head.  You'd have to consider all that was available.  But if

25   they're for emergency purposes, I would probably treat it as

FLORIDA PUBLIC SERVICE COMMISSION

168

1   100 percent used and useful.

2        Q    Would you consider one high service pump 100 percent

3   used and useful?

4        A    Yes.

5             MR. JAEGER:  That's all the questions staff has.

6             CHAIRMAN CARTER:  Commissioners?  Commissioner

7   Argenziano.

8             COMMISSIONER ARGENZIANO:  Yes.  Just a couple of

9   different questions, and I guess maybe for clarification you

10   might be able to help me because to me the requirement for fire

11   flow, I'm going back to fire flow, is the rate of flow

12   theoretically needed to, I guess, successfully combat a major

13   fire at a specific area and that's the way I would --

14             THE WITNESS:  Correct.  Correct.

15             COMMISSIONER ARGENZIANO:  Okay.  So aren't there --

16   or isn't there a fire supression rating schedule that everyone

17   would use?

18             THE WITNESS:  Well, the rating schedules, I mean, go

19   back to 1889 by the National Board of Fire Underwriters and

20   they've been updated in 1922, 1930, 1940, '54, '56, '71.

21             COMMISSIONER ARGENZIANO:  '80?

22             THE WITNESS:  1889 forward.

23             COMMISSIONER ARGENZIANO:  No.  No.  No.  No.  Has it

24   been updated --

25             THE WITNESS:  Updated through 'til today.

FLORIDA PUBLIC SERVICE COMMISSION

169

1             COMMISSIONER ARGENZIANO:  Okay.

2             THE WITNESS:  So today you have the ISO and you have

3   the National Fire Protection Association, all have various fire

4   supression ratings where they actually measure the square

5   footage of the building, the opening, the type of construction

6   material and they go through a very complex analysis of each

7   type of construction size, materials used, openings, what would

8   cause a fire to spread more or less rapidly, and then they also

9   have fire flow requirements that use the classification of the

10   type of construction and different coefficients for these

11   different supression ratings for each building.  And then they

12   determine from those calculations what is the fire flow

13   required.  And that's an integral part of providing fire

14   protection service.  I mean, providing the water is one part,

15   but what type of structure are you, are you dealing with?  And

16   that's what I think many of the local governments would refer

17   to, but many local governments may or may not.  I don't know

18   all of the local governments' requirements.

19             And simply what I'm saying is when that kind of

20   analysis is done, and it's been done now for over 100 years,

21   use what's the most appropriate fire flow requirement based on

22   those analyses that have been performed for thousands upon

23   thousands of community water systems around the country.  Back

24   in 1980 or '56 there were 25,000 community systems that were

25   analyzed.  Now I would guess it's 50,000.  Why not utilize that

FLORIDA PUBLIC SERVICE COMMISSION

170

1   kind of information that tells an engineer and a utility this

2   is the most appropriate fire flow requirement you have for the

3   type of construction that you have that you're serving with

4   your water system.  Use the most appropriate.

5             I think essentially that's what local government, if

6   they're doing it the way I think they should be doing it and

7   probably are, that's what they're referring to.  So rather than

8   just refer to local government, I think including words that

9   say "the most appropriate fire flow" directs the engineer and

10   the utility to the basis for which the utility had incurred

11   costs to meet the fire requirement at that specific area.

12             COMMISSIONER ARGENZIANO:  And just one other

13   question, and I guess I want to see if you agree with this.

14   Our other witness before mentioned that the high service pumps

15   is really just a term, which I kind of tend to agree with

16   because -- and I want to see if you do because I guess if you

17   don't have a separate high service pump, your regular well pump

18   has an additional capacity that then would be the high service

19   pump.  Do you agree with that?

20             THE WITNESS:  I agree with Mr. Woodcock's concept

21   that if you don't have separate high service pumps and you only

22   have wells, those wells are meeting the same demands that a

23   high service pump would be meeting.  But the used and useful

24   rules proposed by staff specifically deal with wells and source

25   of supply.  The term "high service pump" then in the rule was

FLORIDA PUBLIC SERVICE COMMISSION

171

1   treated as a separate item.  So to me the rule is reading

2   you've got provisions in the rule for those systems that have

3   wells and no high service pumps.  If you have a system that has

4   both the wells and then storage facilities and then the high

5   service pumps, then those high service pumps are separate items

6   that are asked to be separated out from the rule.  And I don't

7   think those, that separation is necessary.  By not including a

8   separate rule for high service pumps you're not eliminating the

9   rule for water systems that have wells that effectively serve

10   the same purpose as a high service pump would.

11             COMMISSIONER ARGENZIANO:  Thank you.

12             CHAIRMAN CARTER:  Thank you.  Commissioners?

13             Mr. Hoffman.

14             MR. HOFFMAN:  Thank you, Mr. Chairman.  Just a few on

15   redirect.

16                        REDIRECT EXAMINATION

17   BY MR. HOFFMAN:

18        Q    Mr. Guastella, Mr. Jaeger with the Commission staff

19   asked you a question when you guys were talking about

20   unaccounted for water with an example, I think, of 40 percent

21   unaccounted for water.  I think your testimony essentially was

22   that that might be an unrealistic example and you referred to a

23   75 percent DEP requirement.  Do you recall that exchange with

24   Mr. Jaeger?

25        A    Yes.

FLORIDA PUBLIC SERVICE COMMISSION

172

1        Q    Okay.  The 75 percent DEP requirement, was that a

2   reference to DEP Rule 62-555.348 which addresses planning for

3   expansion of public water systems, source treatment or

4   treatment facilities?

5        A    Yes.  I believe that's the, that's the rule.

6        Q    Okay.  Are you familiar with that rule?

7        A    I am.

8        Q    What does that rule address?

9        A    That rule directs any water utility that if their

10   maximum day demands on the system plus fire flow requirements,

11   if there's a fire flow provision, if that maximum is, reaches

12   75 percent, if the capacity reaches 75 percent of what that

13   maximum demand is anticipated for, the utility has to start

14   reporting to DEP on, within, I believe, six months.  If the

15   report to DEP says that they're going to meet that within ten

16   years, then you have to report again in five years.  If the

17   report shows that the maximum demand is going to be within five

18   years, then you have to report annually to DEP.  And if it's

19   less than five, five years, at some point you have to start

20   providing DEP with actual plans and specifications for

21   constructing expansions of the plant based on the maximum day

22   plus fire demands.

23             MR. HOFFMAN:  Thank you, Mr. Guastella.

24             That's all I have, Mr. Chairman.

25             CHAIRMAN CARTER:  Okay.  Let's deal with the

FLORIDA PUBLIC SERVICE COMMISSION

173

1   exhibits.

2             MR. HOFFMAN:  Aqua would move Exhibits 4 through 7.

3             CHAIRMAN CARTER:  Any objections?

4             MR. FRIEDMAN:  No objection.

5             MR. REILLY:  No objection.

6             MR. JAEGER:  No objection.

7             CHAIRMAN CARTER:  Okay.  So let's show moving into

8   evidence Exhibits 4, 5, 6 and 7.

9             (Exhibits 4, 5, 6 and 7 admitted into evidence.)

10             Commissioners, I'm thinking about that list that you

11   had and I think lunch was on that list.

12             Commissioner Argenziano.

13             COMMISSIONER ARGENZIANO:  Could I ask, in reference

14   to the rule that was just cited, could I ask staff to find out

15   if that's currently being amended by DEP?

16             MS. GERVASI:  We can certainly find that out.

17             COMMISSIONER ARGENZIANO:  Thank you.

18             MS. GERVASI:  Could you repeat the rule number for

19   us, please, Mr. Hoffman?  That will help us.

20             MR. HOFFMAN:  It's Rule 62-555.348.

21             MS. GERVASI:  Thank you.

22             CHAIRMAN CARTER:  Commissioners, I'm thinking in lieu

23   of that we might want to give maybe an extra 15 minutes for

24   staff to bird-dog that.  I'm looking -- believe it or not, I've

25   actually set my clock to the ones on the wall.  So let's look

FLORIDA PUBLIC SERVICE COMMISSION

174

1   at -- I'm looking at 2:20; is that right?  Staff, does that

2   give you ample time to get the information?

3             MS. GERVASI:  Yes, sir.

4             CHAIRMAN CARTER:  Okay.  Let's reconvene at right

5   around 2:20.  We are on recess.

6             (Recess taken.)

7             (Transcript continues in sequence with Volume 2.)

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

175

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

4             I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing proceeding was

5   heard at the time and place herein stated.

6             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

7   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

8   proceedings.

9             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

10   or employee of any of the parties' attorneys or counsel

connected with the action, nor am I financially interested in

11   the action.

12              DATED THIS ________ day of January, 2008.

13

14                  ________________________________

LINDA BOLES, RPR, CRR

15                  FPSC Official Commission Reporter

(850) 413-6734

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION