1

1                              BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3       In the Matter of:

DOCKET NO. 090505-EI

4

REVIEW OF REPLACEMENT FUEL COSTS

5       ASSOCIATED WITH THE FEBRUARY 26,

2008, OUTAGE ON FLORIDA POWER &

6       LIGHT'S ELECTRICAL SYSTEM.

________________________________/

7

8                               VOLUME 1

9                         Pages 1 through 203

10              ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

11               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

12

13

14       PROCEEDINGS:   HEARING

15       COMMISSIONERS

PARTICIPATING: COMMISSIONER LISA POLAK EDGAR

16                      COMMISSIONER NATHAN A. SKOP

COMMISSIONER DAVID E. KLEMENT

17                      COMMISSIONER BEN A. "STEVE" STEVENS III

18       DATE:          Wednesday, March 17, 2010

19       TIME:          Commenced at 9:30 a.m.

20       PLACE:         Betty Easley Conference Center

Room 148

21                      4075 Esplanade Way

Tallahassee, Florida

22

REPORTED BY:   LINDA BOLES, RPR, CRR

23                      JANE FAUROT, RPR

Official FPSC Reporter

24                      850-413-6734/850-413-6732

25

FLORIDA PUBLIC SERVICE COMMISSION

2

1       APPEARANCES:

2                 JOHN T. BUTLER, ESQUIRE, R. WADE LITCHFIELD,

3       ESQUIRE, and MITCHELL S. ROSS, ESQUIRE, Florida Power &

4       Light Company, 700 Universe Boulevard, Juno Beach,

5       Florida 33408-0420, appearing on behalf of Florida Power

6       & Light Company.

7                 VICKI GORDON KAUFMAN, ESQUIRE, Keefe Law Firm,

8       118 North Gadsden Street, Tallahassee, Florida 32301,

9       appearing on behalf of the Florida Industrial Power

10       Users Group.

11                  CECILIA BRADLEY, ESQUIRE, Office of Attorney

12       General, The Capitol - PL01, Tallahassee, Florida

13       32399-1050, appearing on behalf of the Citizens of the

14       State of Florida.

15                 CHARLES J. BECK, ESQUIRE, JOSEPH A.

16       McGLOTHLIN, ESQUIRE, and J. R. KELLY, ESQUIRE, Office of

17       Public Counsel, c/o The Florida Legislature, 111 West

18       Madison Street, Room 812, Tallahassee, Florida

19       32399-1400,  appearing on behalf of the Citizens of the

20       State of Florida.

21                 LISA BENNETT, ESQUIRE, and KEINO YOUNG,

22       ESQUIRE, Florida Public Service Commission, 2540 Shumard

23       Oak Boulevard, Tallahassee, Florida 32399-0850,

24       appearing on behalf of the Florida Public Service

25       Commission Staff.

FLORIDA PUBLIC SERVICE COMMISSION

3

1       APPEARANCES CONTINUED:

2                 MARY ANNE HELTON, DEPUTY GENERAL COUNSEL, FPSC

3       General Counsel's Office, 2540 Shumard Oak Boulevard,

4       Tallahassee, Florida 32399-0850, appearing as advisor to

5       the Commission.

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

4

1                              I N D E X

2       OPENING STATEMENTS:                            PAGE NO.

3       MR. BUTLER                                         12

MR. BECK                                           19

4       MS. BRADLEY                                        26

MS. KAUFMAN                                        29

5

6                              WITNESSES

7       NAME:                                          PAGE NO.

8       JOHN STALL

9       Direct Examination by Mr. Ross                     36

Prefiled Direct Testimony Inserted                 38

10       Errata to Prefiled Direct Testimony Inserted       47

Cross Examination by Mr. Beck                      52

11       Cross Examination by Ms. Bradley                   81

Cross Examination by Ms. Kaufman                   82

12       Cross Examination by Mr. Young                     85

Redirect Examination by Mr. Ross                  105

13

GERARD J. YUPP

14

Direct Examination by Mr. Butler                  110

15       Prefiled Direct Testimony Inserted                113

Cross Examination by Mr. Beck                     121

16       Cross Examination by Ms. Bradley                  127

Cross Examination by Ms. Kaufman                  140

17       Cross Examination by Mr. Young                    145

Redirect Examination by Mr. Butler                167

18

WILLIAM E. AVERA

19

Direct Examination by Mr. Butler                  172

20       Prefiled Direct Testimony Inserted                174

Cross Examination by Mr. McGlothlin               188

21

22

23       CERTIFICATE OF REPORTER (Boles)                   202

24       CERTIFICATE OF REPORTER (Faurot)                  203

25

FLORIDA PUBLIC SERVICE COMMISSION

5

1                              EXHIBITS

2       NUMBER:                                   ID.     ADMTD.

3       1   Comprehensive Exhibit List            32       32

4       2   GJY-1                                112      171

5       3   GJY-2                                112      171

6       4   GJY-3                                112      171

7       5   GJY-4                                112      171

8       6   GJY-5                                112      171

9       7   GJY-6                                112      171

10       8   GJY-7                                112      171

11       9   GJY-8                                112      171

12       10  GJY-9                                112      171

13       26  Staff Exhibit 26                      32       32

14       27  Staff Exhibit 27                      32       32

15       28  Staff Exhibit 28                      32       32

16       29  Staff Exhibit 29                      32       32

17       30  Staff Exhibit 30                      32       32

18       31  Staff Exhibit 31                      32       32

19       32  Staff Exhibit 32                      32       32

20       33  Staff Exhibit 33                      32       32

21       34  Second Deposition of J.A. Stall       33       33

22       35  Deposition of Dr. Dismukes            34       34

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

6

1                         P R O C E E D I N G S

2                 COMMISSIONER SKOP:  Good morning.  I'd like to

3       call this hearing to order.  If staff could please read

4       the notice.

5                 MS. BENNETT:  Pursuant to notice duly given,

6       this day and date was set for the hearing in Docket

7       Number 090505, review of replacement fuel costs

8       associated with the February 26th, 2008, outage on FPL's

9       electric system.

10                 COMMISSIONER SKOP:  Thank you.  If we could

11       now take appearances.

12                 MR. BUTLER:  Thank you, Mr. Chairman.  John

13       Butler appearing on behalf of Florida Power & Light

14       Company.  Also making an appearance for Mitchell Ross

15       and Wade Litchfield.

16                 COMMISSIONER SKOP:  Good morning.

17                 MR. BUTLER:  Good morning.

18                 MR. BECK:  Good morning, Commissioner.  I'd

19       like to make an appearance for myself, Charlie Beck, as

20       well as J. R. Kelly and Joe McGlothlin, Office of the

21       Public Counsel, appearing on behalf of the citizens of

22       Florida.

23                 COMMISSIONER SKOP:  Good morning.

24                 MS. KAUFMAN:  Good morning, Commissioners.

25       Vicki Gordon Kaufman.  I'm with the law firm of Keefe,

FLORIDA PUBLIC SERVICE COMMISSION

7

1       Anchors, Gordon & Moyle, and I'm appearing on behalf of

2       the Florida Industrial Power Users Group.

3                 COMMISSIONER SKOP:  Good morning.  And is the

4       Attorney General's Office making an appearance?

5                 COMMISSIONER STEVENS:  I think she's walking

6       in the door.

7                 COMMISSIONER SKOP:  I believe, I believe she's

8       coming in.

9                 Well, we'll move on to staff and come back to

10       the AG.

11                 MS. BENNETT:  On behalf of staff, Lisa Bennett

12       and Keino Young.

13                 COMMISSIONER SKOP:  All right.

14                 MS. HELTON:  Mary Anne Helton, advisor to the

15       Commission.

16                 COMMISSIONER SKOP:  And Ms. Bradley.

17                 MS. BRADLEY:  Cecilia Bradley, Office of the

18       Attorney General, on behalf of the citizens of Florida.

19                 COMMISSIONER SKOP:  Good morning.  At this

20       point, staff, are there any preliminary matters that we

21       need to address?

22                 MS. BENNETT:  Yes, we have a few.  First I

23       want to note that OPC has filed a request for official

24       recognition of two orders from two other state

25       commissions, Louisiana and Texas.  Now would be the

FLORIDA PUBLIC SERVICE COMMISSION

8

1       appropriate time for the presiding officer to rule on

2       that.

3                 COMMISSIONER SKOP:  Staff recommendation,

4       Ms. Helton?

5                 MS. HELTON:  They seem to me to be appropriate

6       matters for which the Commission can take official

7       recognition, and I don't know of any objections by any

8       of the parties.

9                 COMMISSIONER SKOP:  Any objections by the

10       parties?

11                 MR. BUTLER:  No, FPL does not object.

12                 COMMISSIONER SKOP:  Hearing no objections,

13       we'll take official recognition of the two orders from

14       Louisiana and Texas respectively.

15                 Any other preliminary matters, staff?

16                 MS. BENNETT:  Yes.  There are no objections to

17       the Comprehensive Exhibit List and there are no

18       objections to the admission of staff's Exhibits 26

19       through 33.  We will also have two additional exhibits

20       to be entered into the record when it's -- after opening

21       statements.  We'll deal with that when the record is

22       opened.

23                 COMMISSIONER SKOP:  Very well.

24                 MS. BENNETT:  And additionally, Commissioner

25       Skop, the, at the Prehearing Conference, the parties

FLORIDA PUBLIC SERVICE COMMISSION

9

1       asked that each side be permitted a total of 30 minutes

2       for opening statements and witness summaries with the

3       time divided as each deemed, as each side deemed

4       appropriate.  This morning they gave us a time schedule

5       allocating their 30 minutes per side, and I believe that

6       Mike Staden has it and I think you each have a copy of

7       that time on your dais.

8                 COMMISSIONER SKOP:  All right.  And if the

9       parties are prepared to address the allocation of time

10       and how they're intending to use it, this would probably

11       be the appropriate time.

12                 MR. BUTLER:  Thank you, Mr. Chairman.  For

13       FPL, and I apologize, I'm looking at my BlackBerry

14       because I'm looking at the email I sent to the parties

15       last night and this is the form I have it in, we are

16       proposing ten minutes for opening statements.  And then

17       Mr. Stall's summaries being eight minutes total, four

18       minutes for direct, four minutes for rebuttal; Mr.

19       Yupp's summaries, three minutes total, two minutes for

20       direct and one minute for rebuttal; Mr. Avera's

21       summaries, six minutes total, three minutes for direct

22       and three minutes for rebuttal; and Mr. Keith's

23       summaries, one minute for direct and two minutes for

24       rebuttal, a total of three minutes.  And by my math,

25       that adds up to 30 minutes total.

FLORIDA PUBLIC SERVICE COMMISSION

10

1                 COMMISSIONER SKOP:  Very well.  Thank you.

2                 Mr. Beck.

3                 MR. BECK:  Yes, Commissioner.  We've asked to

4       reserve ten minutes for an opening statement by the

5       Office of Public Counsel, five minutes each for opening

6       statements by the Attorney General and FIPUG, and then

7       ten minutes for a witness summary by Dr. Dismukes.

8                 COMMISSIONER SKOP:   Okay.  Very well.  Thank

9       you.

10                 Staff, any additional preliminary matters?

11                 MS. BENNETT:  As I understand, Mr. Staden will

12       be able to help us keep track of the time with the red,

13       yellow and green lights.

14                 COMMISSIONER SKOP:  Okay.  And as the counsel

15       appearing before us are all seasoned veterans, so you

16       know how this works.  You've got the lights, and when

17       the green light goes on, it's your turn to speak.  When

18       it turns yellow, you have 30 seconds left.  And when the

19       light turns red, you need to conclude and the microphone

20       will be, I guess, turned off, but we're pretty liberal

21       about that.

22                 Commissioners, any additional comments before

23       we get started with opening statements?  Okay.  Plan for

24       the day -- we had a long day at work yesterday.  We need

25       to take a break per the request of one Commissioner at

FLORIDA PUBLIC SERVICE COMMISSION

11

1       approximately 10:00 a.m. for about 15 minutes.  And it's

2       my intent, if the Commission desires, to break for lunch

3       probably from 12:00 to 1:00, 1:30ish depending on the

4       will of my colleagues.  As far as the hearing goes,

5       hopefully we'll conclude within a day, probably go 'til

6       5:00.  But, again, that will be at the discretion of the

7       Commission, having a long day yesterday.  But with that,

8       any other matters that we need to address before we --

9                 MS. BENNETT:  No, Commissioner.  There's no

10       other matters.

11                 COMMISSIONER SKOP:  Okay.  No outstanding

12       motions or petitions?

13                 MS. BENNETT:  We have one confidentiality

14       request.  We believe the document has been returned, so

15       there won't be any other outstanding motions.

16                 COMMISSIONER SKOP:  Okay.  Very well.  And I

17       believe, Ms. Bradley, do you want to reiterate your

18       standing objections?

19                 MS. BRADLEY:  Yes.  I just want to make sure

20       it's on the record that we have objections to late-filed

21       exhibits unless there's an opportunity to cross and

22       present testimony.  And also we objected to the friendly

23       cross reference in the original order.

24                 COMMISSIONER SKOP:  Okay.  And, Ms. Helton, if

25       you could please speak to that and advise the

FLORIDA PUBLIC SERVICE COMMISSION

12

1       Commission.

2                 MS. HELTON:  Yes, Mr. Chairman.  Staff

3       believes that the friendly cross language in the

4       Prehearing Order is appropriate, and I believe that it's

5       appropriate for the presiding officer to address any

6       objections there may be to friendly cross at the

7       appropriate time in the proceeding.

8                 COMMISSIONER SKOP:  Okay.  Very well.  And as

9       far as the late-filed exhibits?

10                 MS. HELTON:  I'm sorry, Mr. Chairman.  I'm

11       still kind of struggling from last night.  The

12       late-filed exhibits, I think that if there are any,

13       those should be addressed at the appropriate time as

14       well when they are raised.

15                 COMMISSIONER SKOP:  Very well.  With respect

16       to late-filed exhibits, again, I recognize the objection

17       of the Attorney General's Office, but we're going to

18       deal with those on a case-by-case basis by ruling of the

19       presiding officer.  And if there is an objection to be

20       raised, it will be a contemporaneous objection.

21                 Okay.  And with that, we'll proceed to opening

22       statements.  And, Mr. Butler, you're recognized.

23                 MR. BUTLER:  Thank you, Commissioner Skop.

24       Good morning, Commissioners.  As you are aware, the

25       Prehearing Officer in the 2009 fuel adjustment docket

FLORIDA PUBLIC SERVICE COMMISSION

13

1       spun off the following issue to be addressed in this

2       docket.  With respect to the February 26th, 2008,

3       outages should FPL or its customers be responsible for

4       replacement power costs associated with the outages?

5       FPL agreed with the parties to this docket that it would

6       bear the cost of replacement power attributable to the

7       February 26th, 2008, outage, what FPL refers to as the

8       Flagami transmission event.

9                 The Commission approved that settlement at its

10       January 26th Agenda Conference, so only two issues

11       remain for resolution in this docket.  One, how should

12       the replacement power costs attributable to the Flagami

13       transmission event be measured and what is the amount of

14       those costs?  And, two, what is the appropriate method

15       to credit customers for the replacement power cost

16       determined pursuant to Issue 1?

17                 FPL's evidence will show that the proper

18       amount of replacement power cost to credit customers is

19       $2,204,035.  FPL's replacement power cost calculation is

20       the fairest to all involved.  It will ensure that

21       customers are promptly credited for replacement power

22       costs attributable to the Flagami transmission event,

23       and it will avoid the disincentives to utility

24       investment in energy efficient and environmentally

25       beneficial generation alternatives that would result

FLORIDA PUBLIC SERVICE COMMISSION

14

1       from adopting the Intervenor's position.

2                 This proceeding involves a fact pattern that

3       appears to be unique among replacement power cost

4       determinations before this Commission.  Typically

5       replacement power costs are incurred because an

6       equipment or operational issue at a power plant has

7       caused an outage at that plant.  The replacement power

8       cost determination is based on an evaluation of the

9       utility's performance in operating and maintaining that

10       plant.  If the utility's operation or maintenance was

11       not prudent, then it must refund to customers the

12       additional fuel and purchased power costs, excuse me, it

13       incurred because that plant was out of service.  The

14       focus is always on the utility's actions at the

15       particular plant in question and on the additional costs

16       associated with the plant being out of service.

17                 Here, however, the evidence will show that

18       FPL's Turkey Point Nuclear Units 3 and 4 were operated

19       prudently and properly.  They came offline automatically

20       as the result of an undervoltage condition caused by the

21       Flagami transmission event.  This was exactly what the

22       nuclear units were designed to do and it's what the

23       Nuclear Regulatory Commission required them to do.

24                 FPL returned the units to service as quickly

25       and safely as possible.  There is no evidence, excuse

FLORIDA PUBLIC SERVICE COMMISSION

15

1       me, that FPL was imprudent either in taking the units

2       offline in response to the undervoltage condition or in

3       bringing them back online thereafter.  The nuclear units

4       performed properly and as expected in response to an

5       external event.

6                 So how should the Commission measure

7       replacement power costs when a prudently operated power

8       plant with very low fuel cost such as a nuclear unit

9       comes offline due to an external event?  FPL's testimony

10       shows that it would be unfair and would discourage

11       investment in such technologies if the Commission were

12       to base replacement power costs on a plant's very low

13       fuel cost.  Doing so would penalize the utility more

14       heavily because the plant which came offline happened to

15       have low fuel costs than would be the case if the same

16       external event had caused a plant with higher fuel costs

17       to come offline instead.

18                 This sort of regulation by lottery should be

19       avoided because it penalizes utilities for the very

20       thing that should be encouraged, which is investing in

21       generation that holds down the fuel costs which

22       customers must pay.

23                 FPL's proposal avoids this problem by basing

24       the replacement power cost calculation on system average

25       costs rather than the avoided fuel cost of the specific

FLORIDA PUBLIC SERVICE COMMISSION

16

1       plant that is out of service.  This way if an external

2       event forces a plant offline, the replacement power cost

3       calculation will be the same regardless of what

4       particular plant happened to be affected.  Under FPL's

5       approach, exposure to replacement power costs is

6       independent of whether the affected plant's fuel costs

7       are high or low, so there is no disincentive for

8       investing in cost-saving efficient generation.

9                 I'd emphasize again this is specifically what

10       we're proposing for this circumstance where you have an

11       external event that causes plants to come out of service

12       not related to anything that is imprudent about the

13       operation of the plants themselves.

14                 You'll hear from Public Counsel and others

15       throw around the term "windfall" in describing FPL's

16       replacement power cost calculation.  Let me assure you

17       that the term doesn't fit.  FPL has not recovered a

18       penny more than its actual fuel costs incurred for the

19       Flagami transmission event, and now FPL has agreed to

20       give customers back more than $2 million of those fuel

21       costs.  Being out of pocket for more than $2 million in

22       actual incurred fuel costs is certainly no windfall to

23       FPL or its shareholders.  Excuse me.

24                 What Public Counsel and the other Intervenors

25       ignore on the other hand are the enormous benefits that

FLORIDA PUBLIC SERVICE COMMISSION

17

1       FPL's customers have received from the operation of

2       Turkey Point Units 3 and 4, both over time and

3       specifically in 2008 when the Flagami transmission event

4       occurred.

5                 FPL's testimony will show that Turkey Point

6       Units 3 and 4 have saved FPL's customers about

7       $7.7 billion in fuel costs since 1990, and those units

8       have actually been in service for approximately twice

9       that long.  Focusing specifically on 2008, FPL's

10       testimony will show that Turkey Point Units 3 and 4 had

11       a combined capacity factor of 93.41 in that year, which

12       is almost 3.5 percentage points above the 2008 nuclear

13       industry average.

14                 This superior performance translates into

15       about $25 million in 2008 fuel savings for FPL customers

16       compared to industry average performance, in spite of

17       the outages that were initiated by the Flagami

18       transmission event.  Simply put, FPL has proposed a

19       reasonable, fair approach to calculating replacement

20       power costs for the Flagami transmission event, one that

21       will appropriately compensate customers for the

22       consequences of that event, while not discouraging

23       continued investment in environmentally friendly

24       generation technologies that have low fuel costs.  The

25       enormous fuel cost savings that FPL's nuclear units

FLORIDA PUBLIC SERVICE COMMISSION

18

1       bring to its customers cannot be ignored in achieving a

2       balanced position or a balanced solution.  FPL's

3       approach strikes a fair balance, while the Intervenors'

4       opportunistic approach does not even strive for balance.

5       The Commission should adopt FPL's balanced approach

6       because it is in the longterm best interest of FPL's

7       customers and the environmental goals of the State of

8       Florida.

9                 Before I conclude, let me turn briefly to

10       Issue 2:  How, how FPL should refund the credit that the

11       Commission determines appropriate.  FPL believes that

12       the most straightforward approach is to flow the credit

13       through the regular fuel adjustment true-up mechanism

14       where it will serve to reduce customers' bills

15       throughout 2011.  If the Commission decides instead to

16       use a one-time refund, then the refund should be applied

17       to electric consumption that is billed in the month the

18       refund takes place.  The Commission approved this

19       approach for FPL's last two refunds, and it is the

20       fastest and best way to return the refund to customers.

21       Thank you for the opportunity to address you this

22       morning.

23                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

24                 We'll proceed now with opening statement from

25       Public Counsel.  Mr. Beck.

FLORIDA PUBLIC SERVICE COMMISSION

19

1                 MR. BECK:  Thank you, Commissioners, and good

2       morning.  The issue before you today is whether Florida

3       Power & Light or its customers will pay for the

4       additional replacement fuel and power costs associated

5       with an outage that occurred on February 26th, 2008.

6       You're going to hear testimony from four different

7       Florida Power & Light witnesses, you're going to hear it

8       many times because they're both on direct and rebuttal,

9       and you'll hear testimony from our expert witness,

10       Dr. David Dismukes.  Now despite the disputes that

11       you're going to hear in the testimony, there's really

12       quite a few items on which there's no agreement between

13       Florida Power & Light and our office and the other

14       Intervenors.

15                 First of all, there's no dispute about the

16       cause of the outage.  According to what is Exhibit 12,

17       which is an attachment to Dr. Dismukes' testimony, and

18       that's a $25 million settlement agreement which FP&L

19       reached with the Federal Energy Regulatory Commission

20       and the North American Electric Reliability Corporation,

21       according to the facts that are set forth in that

22       exhibit, on February 26th, 2008, a Florida Power & Light

23       employee was sent to test a circuit switcher at the

24       Flagami substation, which is located in Western Miami.

25       Once there, he disabled both primary circuit protection

FLORIDA PUBLIC SERVICE COMMISSION

20

1       and breaker failure protection, which is considered a

2       secondary level of protection.  He didn't tell the load

3       dispatcher that he had disabled the secondary level of

4       protection as well as the primary protection and the

5       load dispatcher didn't tell the system operator that any

6       of the protection had been disabled.  A fault occurred

7       during the work which caused a 17- to 19-second arc, and

8       that led to a three-phase fault on the 138 kilovolt

9       system.  This led to significant frequency swings which

10       tripped transmission and generation around portions of

11       the lower two-thirds of Florida, including significant

12       lengthy outages at the two Turkey Point nuclear plants.

13       Almost one million customers of Florida Power & Light

14       and other electric utilities were without service for

15       some period of time.

16                 There's also no dispute about the amount of

17       time that two nuclear reactors at Turkey Point were out

18       of service.  Unit Number 3 was out for approximately 158

19       hours and Unit Number 4 was out for approximately 107

20       hours.  During that time, expensive replacement power

21       had to be procured either by purchasing power or by

22       running other units whose fuel costs were many, many

23       times the cost of the fuel used in nuclear generation.

24                 There's also very little dispute about the

25       extra amount of fuel expense that was incurred as a

FLORIDA PUBLIC SERVICE COMMISSION

21

1       result of the outage.  Dr. Dismukes will sponsor

2       testimony showing the net extra expense was

3       approximately $15.9 million using the outage times and

4       data provided by Florida Power & Light.  There's also an

5       estimate that was produced by Florida Power & Light in

6       response to a data request from staff.  Florida Power &

7       Light ran a computer simulation which did an

8       hour-by-hour reconstruction of what actually happened

9       compared to what would have happened had there been no

10       outage.  That simulation shows an extra replacement cost

11       of approximately $14.5 million.  You'll hear about that

12       during the cross-examination of Florida Power & Light's

13       Witness Yupp.

14                 The primary difference between the two

15       estimates is attributable to the use of ascension power

16       levels during the restart of the two units in the

17       computer simulation, while the estimate by Dr. Dismukes

18       did not have that information available.  Both estimates

19       are close, $15.9 million versus $14.5 million, and we

20       know the reasons for the differences between the two

21       estimates.

22                 Finally, there's another item of agreement

23       between Florida Power & Light and Intervenors.  Florida

24       Power & Light, to its credit, entered into an agreement

25       with Intervenors this past December to accept

FLORIDA PUBLIC SERVICE COMMISSION

22

1       responsibility for the replacement power costs, and the

2       Commission approved that agreement in January.

3                 With agreement on so much of the case, you

4       might wonder why we're here.  The reason we're here is

5       that Florida Power & Light's notion of accepting

6       responsibility for the cost of replacement power is

7       vastly different than ours.  Despite the fact that we

8       know the cost of replacement power attributable to the

9       actions of Florida Power & Light's engineer, and it's in

10       the ball park of $15 million, Florida Power & Light will

11       only accept responsibility for about $2 million and

12       would leave customers holding the bag for about

13       $13 million of extra cost.

14                 There are two reasons for this.  First,

15       Florida Power & Light doesn't want to measure the cost

16       of replacement power against the cost of running the

17       nuclear units.  They want you to measure the replacement

18       power costs against average system cost, which in

19       essence means that they want you to pretend that the

20       nuclear plants didn't go down.  Well, they did go down,

21       each for over 100 hours, and the proper measure of extra

22       cost should be compared to the fuel cost to run the

23       nuclear plants.

24                 The second reason for the vast difference in

25       our ideas of what it means to be responsible for

FLORIDA PUBLIC SERVICE COMMISSION

23

1       replacement power costs is that Florida Power & Light

2       only wants to be responsible for the first eight hours

3       of the outage instead of the actual length of the

4       outage, which included an outage of 158 hours at Turkey

5       Point Unit 3 and 107 hours at Turkey Point Unit 4.

6                 How does Florida Power & Light justify this?

7       For one thing, they claim it would be unfair for them to

8       be accountable for the nuclear plants going down when

9       the cause of the outage is related to transmission; that

10       holding them accountable for the actual consequences of

11       the outage caused by the actions of their engineer would

12       be a disincentive for them to invest in nuclear and

13       renewable energy sources.  The standard underlying

14       utility regulation doesn't permit such a parsing and

15       dicing of the utility's responsibility.  Obviously a

16       transmission event can lead to generation consequences

17       in the form of higher replacement costs.  When that

18       occurs, the role of the regulator it to insulate

19       customers from bearing unreasonable costs.  Having

20       accepted responsibility for the costs attributable to

21       the Flagami episode, Florida Power & Light is now trying

22       to carve out exceptions regarding their responsibility.

23                 If the blackout, which was precipitated by the

24       actions of their engineer, led to two nuclear plants

25       going down and the necessity to procure expensive

FLORIDA PUBLIC SERVICE COMMISSION

24

1       replacement power, Florida Power & Light must accept

2       responsibility for that.

3                 They also contend that if they're required to

4       be fully responsible for the replacement costs for fuel,

5       it will create a disincentive to invest in nuclear and

6       renewable energy sources.  This is perhaps the most

7       dangerous of FP&L's arguments because clearly they hope

8       to avoid not only the disallowance in this case, but to

9       create a precedent that will protect it in future

10       proceedings.

11                 The provision of nuclear energy and renewable

12       energy generally require high levels of capital, and the

13       lower cost of fuel helps to partially offset those

14       higher capital costs.  Nothing in this case affects the

15       company's capital recovery for these investments or the

16       profit level they earn on those investments.  Florida

17       Power & Light will earn the same profit on its

18       investment in nuclear power if the Commission protects

19       customers against the higher fuel costs and replacement

20       power costs incurred as a result of the outage.

21       Customers will continue to pay the company for their

22       investment in the nuclear power.  Protection of

23       customers against high fuel and replacement power costs

24       incurred because of the blackout doesn't involve one

25       dollar of disallowing nuclear power costs.

FLORIDA PUBLIC SERVICE COMMISSION

25

1                 The insulation that Florida Power & Light

2       seeks is not designed to present -- or prevent a

3       disincentive.  With this argument, Florida Power & Light

4       is trying to accomplish a paradigm shift.  It wants to

5       rewrite the fundamental ratemaking equation so as to

6       incorporate an exception for specific generation

7       technologies.  But the Commission should see this effort

8       for what it is.  It's not a perceived disincentive.

9       Instead, it's another garden variety attempt to shift

10       the risk of mismanagement, which has always been on the

11       company and which is well understood by investors, from

12       the utility to its customers, and the Commission should

13       reject this effort.

14                 There's really but one question in front of

15       the Commission.  We know that there are damages of

16       approximately $15 million, higher costs that have

17       already been passed on to customers.  Someone is going

18       to be responsible for that.  It is either going to be

19       Florida Power & Light or it's going to be its customers.

20       We hope you'll find that Florida Power & Light is the

21       responsible party for those costs.  Thank you.

22                 COMMISSIONER SKOP:  Thank you, Mr. Beck.  I

23       believe it's 10:00, but I'd like to move forward with

24       getting the two opening statements from the AG and

25       FIPUG, and I think that'll put us at 10:10 and we'll

FLORIDA PUBLIC SERVICE COMMISSION

26

1       take a break.

2                 Ms. Bradley, you're recognized for opening

3       statements.

4                 MS. BRADLEY:  Thank you.  This is similar to a

5       case that we did before some of our members were,

6       Commissioners were on there, but Florida Power & Light

7       had what we referred to as the drilled hole case.  A

8       person had been granted unescorted access and drilled a

9       hole that caused some problems and outages.  This, like

10       that case, was a preventable event.

11                 The citizens do not have control over the

12       employees and the policies.  It is Florida Power & Light

13       that does.  And this was clearly one of their employees

14       that caused this event.  They are the ones that have

15       control over that, certainly not the citizens.  So it's

16       only fair that the people responsible are the ones that

17       have to pay for this.  It's not intended as a

18       disincentive but as an encouragement to be very careful

19       when we're dealing with our power, especially power that

20       affects our nuclear plants.  We have citizens that are

21       concerned about nuclear.  They have not accepted the

22       fact that this is the, the new future for Florida.  But

23       our Legislature, our Cabinet officials are very

24       pronuclear and see this as a tremendous opportunity for

25       Florida.

FLORIDA PUBLIC SERVICE COMMISSION

27

1                 But it's important that the citizens know that

2       this is a safe power alternative for Florida.  And in

3       order that we ensure them of that, we have to strictly

4       comply with the rules and make sure that policies are

5       strictly enforced.  And clearly this particular event

6       was a preventable event.

7                 It was referred to as an external event, but

8       it wasn't.  It was a Florida Power controlled event.

9       The federal officials have looked at it and determined

10       that they were responsible.  There's no question about

11       that.  And this was not a minor problem.  This was a

12       catastrophic event.  We had power outages in Central and

13       South Florida and suddenly cities were without power for

14       important things such as traffic lights.  There were a

15       number of accidents because suddenly the power goes out,

16       the traffic lights go out and we have all these

17       problems.  And because this was a preventable event, it

18       was something that could have been avoided.  And because

19       Florida Power & Light was responsible, they should be

20       responsible for the, the cost of this.

21                 There's been discussion and you'll hear in the

22       testimony that, well, this was not any different from

23       the regular shutdowns that they do.  But it was

24       different.  It's kind of like saying that if you have a

25       big event coming up and all of the sudden at the last

FLORIDA PUBLIC SERVICE COMMISSION

28

1       minute you have to run out and do replacement purchases,

2       you're going to pay more probably.  If you plan ahead of

3       time, you have an opportunity to essentially shop around

4       and find the best price you can.  But because this was a

5       sudden, unexpected event, they had to get what they

6       could at that point as far as replacement costs, and

7       that has increased the amount of money that the citizens

8       have been charged for this.

9                 Again, I would emphasize the fact that this

10       was like the drilled hole case.  I would ask that the

11       refunds be done on a one-time event.  And unfortunately

12       with the drilled hole case we had an issue that came up

13       at the last minute about how this was to be determined,

14       and in order to get the citizens their money as quickly

15       as possible we had to reach some compromises in that.

16       But I would ask that you plan ahead of time and consider

17       the fact that this can be determined over a longer

18       period of time.  We felt it was unfair at that time to

19       just look at the short period of time that they, that we

20       had to look at in determining that.  And I think staff

21       had also recommended that it be determined over a longer

22       period of time so it would be fairer to the customers.

23       So we would ask that you do a one-time as quickly as

24       possible and determined according to the period of time.

25       Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

29

1                 COMMISSIONER SKOP:  Thank you, Ms. Bradley.

2                 Ms. Kaufman, you're recognized for opening

3       statements.

4                 MS. KAUFMAN:  Thank you, Commissioner.  Good

5       morning again, Commissioners.  As I said earlier, I'm

6       here on behalf of the Florida Industrial Power Users

7       Group.  I'm not going to reiterate what Mr. Beck and

8       Ms. Bradley have already told you.  FIPUG agrees with

9       and we support the position of the Public Counsel in

10       this case and the testimony and the position of their

11       witness, Dr. Dismukes.

12                 From our perspective, as we looked at this

13       case from a high level, we think that the main thing to

14       keep in mind here when you decide who should bear the

15       responsibility for these costs is that the event, as FPL

16       likes to call it, that happened at Flagami would not

17       have occurred had it not been for the behavior of FPL

18       employees.  That means that the nuclear units would not

19       have tripped offline on February 26th, 2008, had those

20       employees acted appropriately.  As a result of this

21       behavior, the transmission fault led to the loss of 22

22       transmission lines, 4,300 megawatts of generation and

23       3,650 megawatts of customer load.  You can find all that

24       information in the FERC stipulation that Florida Power &

25       Light entered into.

FLORIDA PUBLIC SERVICE COMMISSION

30

1                 It seems to us that FPL is attempting to say

2       that what Mr. Butler called the external event was

3       something that happened that was totally beyond Florida

4       Power & Light's control and it was unrelated to Florida

5       Power & Light or its operations, but we know that that

6       is not the case.  And if you look at the FERC

7       stipulation, you will see FPL paid a $25 million fine

8       and agreed to undertake a number of reliability

9       activities.  We think that that agreement is significant

10       and you should consider it when you decide how to deal

11       with the replacement fuel costs that customers are

12       facing here.

13                 As I said, if the employee had, employees had

14       not made the error, we wouldn't even be here today.  The

15       nuclear units would have continued to operate and they

16       would have provided low cost fuel to FPL customers.  And

17       so in our view that means that FPL should be responsible

18       for reimbursing the customers for the replacement fuel

19       costs for the 158 hours that Turkey Point Unit 3 was off

20       and the 107 hours that Turkey Point Unit 4 was off.  To

21       do otherwise would be, as I think others have said,

22       place responsibility on the customers, not on the

23       utility.

24                 And Mr. Butler made some comments about the

25       cost savings that these units have provided to

FLORIDA PUBLIC SERVICE COMMISSION

31

1       customers.  And I think we all know and we agree that

2       nuclear units have low fuel costs, and that's one of the

3       reasons that the utilities come to you and ask you in

4       determinations of need to approve these facilities.  I

5       would also point out to you, however, that Turkey Point

6       Unit 3 and 4 have been in Florida Power & Light's rate

7       base and have been paid for by customers, as well as

8       customers have paid for a return on these plants for

9       some time, and thus customers expect to receive low fuel

10       costs from these plants and they expect to see these

11       units operating appropriately.

12                 So we support Dr. Dismukes' calculation and we

13       think that you should require Florida Power & Light to

14       reimburse the ratepayers for, it's approximately $15 to

15       $16 million of actual replacement costs that were

16       incurred, and we also support the one-time return,

17       return of this money to the ratepayers.  Thank you.

18                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

19       At this point we'll stand in recess and we'll reconvene

20       at 10:30.  Thank you.

21                 (Recess taken.)

22                 COMMISSIONER SKOP:  Okay.  We're going to go

23       back on the record.  And where we left off, we had

24       finished with opening statements and are going to move

25       forward with exhibits.

FLORIDA PUBLIC SERVICE COMMISSION

32

1                 Staff?

2                 MS. BENNETT:  Yes, Commissioners.  The

3       Comprehensive Exhibit List all the parties have agreed

4       to, we would ask that that Comprehensive Exhibit List be

5       marked as Number 1 and moved into the record at this

6       time.

7                 COMMISSIONER SKOP:  So moved.

8                 (Exhibit Number 1 marked for identification

9       and admitted into the record.)

10                 MS. BENNETT:  And then staff has Exhibits 26

11       through 33.  We would ask -- and all of the parties have

12       agreed to the admission of those into the record -- we

13       would ask that these be moved into the record at this

14       time.

15                 COMMISSIONER SKOP:  Okay.  Any objection from

16       the parties?

17                 MR. BUTLER:  No.

18                 COMMISSIONER SKOP:  Hearing none, so moved.

19                 (Exhibit Numbers 26 through 33 marked for

20       identification and admitted into the record.)

21                 MS. BENNETT:  And next we have Staff's Exhibit

22       Number 34.  It is the second deposition of Mr. Stall.

23       We would ask that that be marked as Exhibit 34.  The

24       title is second deposition of J. A. Stall marked as

25       Exhibit 34 and moved into the record at this time.

FLORIDA PUBLIC SERVICE COMMISSION

33

1                 COMMISSIONER SKOP:  Any objections to entering

2       what has been marked as Exhibit 34 into the record?

3                 MR. BUTLER:  No objection.

4                 COMMISSIONER SKOP:  Hearing none, Exhibit 34

5       will be entered into the record.

6                 (Exhibit Number 34 marked for identification

7       and admitted into the record.)

8                 COMMISSIONER SKOP:  Staff.

9                 MS. BENNETT:  And then by agreement of all the

10       parties, Florida Power and Light would like to admit the

11       deposition of Doctor Dismukes into the record.  I'll let

12       Mr. Butler address that.

13                 COMMISSIONER SKOP:  Mr. Butler, you're

14       recognized.

15                 MR. BUTLER:  Thank you, Commissioner Skop.

16                 Yes.  FPL would move the admission of Doctor

17       Dismukes' deposition transcript into the record just

18       sort of to complete the package.  We have the deposition

19       transcripts of the other witnesses who were deposed in

20       the record as exhibits and think that it would be

21       appropriate to do so likewise with respect to Doctor

22       Dismukes.

23                 COMMISSIONER SKOP:  Okay.  Any objection from

24       the parties?

25                 Ms. Kaufman, you're recognized.

FLORIDA PUBLIC SERVICE COMMISSION

34

1                 MS. KAUFMAN:  Commissioner Skop, I don't have

2       any objection.  But, Mr. Butler, will you be providing

3       copies of the deposition?

4                 MR. BUTLER:  I have them here and I will hand

5       them out at this point.

6                 Staff, can we have somebody hand them out,

7       please.  And I'm sorry, I do not have cover pages on

8       them.  It would be 35.  If you would like I can bring

9       them back with cover pages later or we can just mark 35.

10                 COMMISSIONER SKOP:  Staff, what's your

11       preference?

12                 MS. BENNETT:  I think we can just write Number

13       35 on top of the deposition transcript and be fine with

14       it.

15                 COMMISSIONER SKOP:  Okay.  Very well.  Hearing

16       no objection, Exhibit 35 will be admitted into the

17       record.

18                 MR. BUTLER:  Thank you.

19                 (Exhibit Number 35 marked for identification

20       and admitted into the record.)

21                 COMMISSIONER SKOP:  Staff, any other exhibits

22       that we need to take up at this time?

23                 MS. BENNETT:  No.  All of the other exhibits

24       are listed and will be entered into the record by the

25       party as they present their testimony.

FLORIDA PUBLIC SERVICE COMMISSION

35

1                 COMMISSIONER SKOP:  Very well.  At this point

2       I'd like to swear in the witnesses.

3                 FPL, do you have all of your witnesses

4       available?

5                 MR. ROSS:  We do.

6                 COMMISSIONER SKOP:  The intervenors?  Okay.

7       If the witnesses could all stand, and I'll ask you to

8       raise your right hand.

9                 (Witnesses sworn collectively.)

10                 COMMISSIONER SKOP:  Thank you.

11                 Staff, with respect to the order of

12       witnesses --

13                 MS. BENNETT:  We suggest that they be taken up

14       as they appear in the prehearing order, so I believe Mr.

15       Stall would be up first for FPL.

16                 COMMISSIONER SKOP:  Very well.

17                 Mr. Butler, do you want to call your first

18       witness?

19                 MR. BUTLER:  Thank you, Commissioner Skop.

20       And Mr. Ross will be handling the presentation of Mr.

21       Stall.

22                 MR. ROSS:  Good morning, Mr. Chairman.

23                 FPL calls Art Stall.

24                 COMMISSIONER SKOP:  Very well.

25                 MR. ROSS:  Mr. Chairman, while Mr. Stall is

FLORIDA PUBLIC SERVICE COMMISSION

36

1       taking the stand, we have copies of the errata sheet

2       that was filed with respect to Mr. Stall's direct

3       testimony, and I would request that those be passed out

4       for the convenience of the parties and the

5       Commissioners.

6                 COMMISSIONER SKOP:  Yes.

7                            JOHN A. STALL

8       was called as a witness on behalf of FPL, and having

9       been duly sworn, testified as follows:

10                         DIRECT EXAMINATION

11       BY MR. ROSS:

12            Q.   Please state your name and business address.

13            A.   My name is John A. Stall, 700 Universe

14       Boulevard, Juno Beach, Florida.

15            Q.   And, Mr. Stall, have you prepared Direct

16       Testimony in this proceeding totaling nine pages?

17            A.   I have.

18            Q.   And did you file errata to your Direct

19       Testimony on March 2nd, 2010?

20            A.   I did.

21            Q.   Other than the changes noted in the errata

22       sheet, do you have any other changes or corrections to

23       your Direct Testimony?

24            A.   No.

25            Q.   If I asked you the questions contained in your

FLORIDA PUBLIC SERVICE COMMISSION

37

1       corrected Direct Testimony today, would your answers be

2       the same?

3            A.   Yes.

4                 MR. ROSS:  Mr. Chairman, I would request the

5       Direct Testimony of Mr. Stall as amended by the errata

6       be entered into the record as if read.

7                 COMMISSIONER SKOP:  Let it be done that the

8       prefiled testimony of Mr. Stall will be entered into the

9       record as though read.

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

50

1       BY MR. ROSS:

2            Q.   Mr. Stall, have you prepared a summary of your

3       Direct Testimony?

4            A.   I have.

5            Q.   Would you please provide that summary to the

6       Commission.

7            A.   Good morning, Commissioners.

8                 My testimony explains how Turkey Point Units 3

9       and 4 were prudently and properly taken off-line in

10       response to the voltage fluctuations caused by the

11       February 26th, 2008, transmission event that was

12       initiated at FPL's Flagami Substation.  I also explain

13       the equipment issues that emerged during the outage that

14       were independent of the Flagami event and delayed the

15       restart of the Turkey Point nuclear units.

16                 As a result of the Flagami event, Turkey Point

17       Units 3 and 4 automatically shut down to protect

18       safety-related equipment precisely as designed and in

19       accordance with the Nuclear Regulatory Commission

20       operating licenses for Units 3 and 4.  FPL then took

21       prudent and conservative measures to investigate,

22       inspect, and analyze the plant prior to safely

23       restarting both units.

24                 The Nuclear Regulatory Commission had no

25       issues with the outages or the restart of either unit.

FLORIDA PUBLIC SERVICE COMMISSION

51

1       It usually takes approximately 48 hours to bring a

2       single nuclear unit back on-line after an unexpected

3       plant shutdown.  However, it is not uncommon for

4       unrelated equipment issues to delay the restart of a

5       reactor.

6                 The Unit 3 outage was extended to repair the

7       rod position indication system that had previously

8       malfunctioned in October of 2007.  At FPL's request, the

9       Nuclear Regulatory Commission amended the Unit 3

10       operating license to allow FPL as an interim measure to

11       continue operating the plant contingent upon a

12       commitment to repair the RPI system the next time the

13       unit shut down.  After the Flagami event, the RPI repair

14       was conducted and the unit was returned to service

15       without incident.

16                 When Unit 4 was returning to service, there

17       was a turbine shutdown attributable to a relay problem,

18       and plant operators subsequently initiated a manual

19       reactor trip because of high steam generator water level

20       as required by plant procedures.  A reactor shutdown in

21       these circumstances is not unusual.

22                 While our goal is to run our nuclear units for

23       their entire 18-month fuel cycle in order to maximize

24       the fuel cost savings for our customers, this is not

25       always possible.  Unscheduled shutdowns are not evidence

FLORIDA PUBLIC SERVICE COMMISSION

52

1       of problems or deficiencies in either the design or

2       operation of nuclear units.  Rather, those shutdowns

3       demonstrate that safety systems are working properly and

4       that plant operators are trained to and exhibit the

5       right behaviors to conservatively operate these nuclear

6       units.

7                 The generation performance of both Turkey

8       Point Units 3 and 4, as measured by the capacity factor

9       and the equivalent availability factor, were

10       significantly above industry averages in 2008 despite

11       the unexpected outages from the Flagami Transmission

12       event.  These statistics illustrate that FPL's customers

13       have received the benefit of considerably more low-cost

14       nuclear generated energy in 2008 than they would have if

15       Units 3 and 4 had performed at industry averages.

16                 This concludes my summary.

17                 COMMISSIONER SKOP:  Thank you.

18                 MR. ROSS:  We tender the witness for cross

19       examination.

20                 COMMISSIONER SKOP:  Mr. Beck, you're

21       recognized.

22                 MR. BECK:  Thank you, Commissioner.

23            BY MR. BECK:

24            Q.   Good morning, Mr. Stall.

25            A.   Good morning, Mr. Young (sic).

FLORIDA PUBLIC SERVICE COMMISSION

53

1            Q.   I'm Charlie Beck.

2            A.   Oh, I'm sorry.

3            Q.   But, good morning.  How are you this morning?

4            A.   Good morning, Mr. Beck.

5            Q.   Mr. Stall, I'd like to ask you to turn to Page

6       3 of your testimony at Lines 15 and 16.  And I believe

7       you mentioned this in your summary, as well.  You state

8       that it typically takes approximately 48 hours to bring

9       a single unit back on-line after an unexpected plant

10       shutdown.  Is that correct?

11            A.   That is correct.

12            Q.   That time period you give there does not

13       include the ramp-up time to bring the power plant up to

14       full power, does it?

15            A.   That's correct.  That's typically

16       breaker-to-breaker, what we call breaker-to-breaker,

17       from the breaker opening to the breaker closing.

18            Q.   And the breaker closing would be when the

19       reactor connects to the grid, as it were?

20            A.   That's correct.  And then we would go through

21       the power ascension process.

22            Q.   And the power ascension process, does that

23       take approximately 12 to 14 hours?

24            A.   That's correct.

25            Q.   You've stated that that is the amount of time

FLORIDA PUBLIC SERVICE COMMISSION

54

1       to bring a single unit back on-line, but in this case we

2       had two of them that had to be brought back on-line.  Is

3       that right?

4            A.   That's correct.

5            Q.   And when you have to bring two units back

6       on-line after an unexpected shutdown, that will

7       typically take three to five days, does it not?

8            A.   That's correct.  And that's highly dependent,

9       of course, upon the nature of the event that caused the

10       shutdowns as well as the maintenance that would need to

11       be performed during that period of time and the

12       surveillance testing.  And, of course, with two units

13       out of service, it's highly dependent upon the resources

14       that you have because you have a fixed amount of

15       resources available, and now you have to attend to two

16       units versus just one.

17            Q.   On Page 4 of your testimony, at the top you

18       talk about special training that is done during the

19       start up of the reactors, is that right?

20            A.   Yes.

21            Q.   And that training adds incremental time or

22       incremental time to a start-up after an unexpected plant

23       shutdown, does it not?

24            A.   Not necessarily.  We generally are able to

25       manage that training within the critical path of the

FLORIDA PUBLIC SERVICE COMMISSION

55

1       overall outages.  In other words, we'll take the crew

2       that we believe will be in the control room at the time

3       of reactor start-up and manage to get them over to the

4       simulator even while these other activities are going on

5       in the plant, so that's not necessarily an additive

6       time.

7            Q.   Well, let me ask you, does your testimony on

8       Page 4, Lines 4 through 5, don't you state that it adds

9       incremental time to the plant start-up consequence after

10       an unplanned reactor shutdown?

11            A.   In this particular case because there were two

12       units out of service that would be true, but I thought

13       you were asking generically.  Generically, it's not

14       always the case that it would add incremental time.

15            Q.   So if you had a planned shutdown it typically

16       would not add incremental time, would it?

17            A.   It would depend upon the nature of that

18       shutdown and the amount of work that needed to be done.

19       But there is no one-size-fits-all, if you understand

20       what I'm saying, to be able to say in all cases it would

21       add incremental time.  In this case that would be true

22       because of the dual unit outage.

23            Q.   You conducted what I think you have termed

24       just-in-time training, is that right, for the operators?

25            A.   Correct.

FLORIDA PUBLIC SERVICE COMMISSION

56

1            Q.   Would you describe that, please?

2            A.   What just-in-time training is that, again, we

3       would look ahead on the schedule and we would anticipate

4       the period of time where we would be starting up the

5       reactor and placing it back in service.  And we would

6       get the crew that would be in the control room over to

7       the simulator and we would have them do a start up on

8       the simulator just before we were to do that training.

9       That training is not required by the Nuclear Regulatory

10       Commission, and it is a best practice that we attempt to

11       do each time we have a start-up that we know about that

12       is intended or planned.

13            Q.   So in one sense would it be fair to say that

14       that's a practice run, in essence, before the operators

15       go and do the real thing?

16            A.   That's correct.

17            Q.   At Page 6 of your testimony beginning at

18       Line 16, you mention that the outage for Unit 4 was

19       extended because the water level in one of the four

20       steam generators exceeded 75 percent, is that right?

21            A.   Yes.

22            Q.   Did Florida Power and Light conduct a root

23       cause analysis to determine what led to the steam

24       generators exceeding 75 percent water level?

25            A.   Yes, we did.

FLORIDA PUBLIC SERVICE COMMISSION

57

1            Q.   Okay.  I'd like to -- I'm going to hand you an

2       excerpt from what has been admitted into evidence as

3       Exhibit 31.  I think it's on the CD that the staff has

4       handed out, and the excerpt is going to start at Bates

5       stamp 410 of the exhibit.

6                 COMMISSIONER SKOP:  Mr. Beck, if you have

7       additional hard copies that might be beneficial for the

8       Commission.

9                 MR. BECK:  I didn't make many copies because

10       we were all -- the idea was to use CDs and not make

11       paper.

12                 COMMISSIONER SKOP:  Commissioners, are you

13       comfortable with that, or would you like a hard copy?

14                 COMMISSIONER STEVENS:  I'm fine.

15                 COMMISSIONER SKOP:  Commissioner Edgar.

16                 COMMISSIONER EDGAR:  We'll try it this way,

17       and if we need a hard copy, then I will be glad to ask.

18                 Thank you, Mr. Beck.

19                 MR. BECK:  I have one extra here,

20       Commissioner, if you'd like that.

21                 COMMISSIONER SKOP:  Thank you.

22                 COMMISSIONER EDGAR:  I'm old fashioned, so if

23       you have an extra copy I will take it, but I don't want

24       to be the reason for the death of more trees, either.

25                 COMMISSIONER SKOP:  No, that's fine.  I've got

FLORIDA PUBLIC SERVICE COMMISSION

58

1       one.  I just thought that we were all trying to do the

2       CD thing this time.

3                 COMMISSIONER EDGAR:  Thank you.

4                 COMMISSIONER SKOP:  Thank you, Mr. Beck.  You

5       may proceed.

6       BY MR. BECK:

7            Q.   Mr. Stall, do you have the exhibit I just

8       handed you?

9            A.   Yes.

10            Q.   And, again, Commissioner, this doesn't have

11       the Bates stamps because that was on the CD, but this

12       begins with the Florida Power and Light Bates stamp of

13       10-83, does it not?

14            A.   On the bottom of the first page?  Yes, that is

15       correct.

16            Q.   And this is an excerpt from the root cause

17       analysis behind the 75 percent water level in the steam

18       generator, is it not?

19            A.   Yes, it is.

20            Q.   Let me ask you to go to what on your copy has

21       10-85 on it, and that would be Bates-stamped 4-12 of the

22       staff exhibit.

23            A.   Okay.

24            Q.   And I'd like to ask you about the second

25       paragraph from the top where it starts, "This manual

FLORIDA PUBLIC SERVICE COMMISSION

59

1       reactor trip," do you see that?

2            A.   I see that.

3            Q.   Okay.  It says this manual reactor trip

4       challenged plant systems and caused financial

5       consequences by adding an unplanned unit cycle and

6       delaying start up of both Turkey Point nuclear units by

7       approximately 30 hours.  Do you see that?

8            A.   I do.

9            Q.   What does it mean by challenged plant systems?

10            A.   Well, any time you actuate a safety system, in

11       this particular case the manual reactor trip is what we

12       are talking about, the safety systems are exercised.  So

13       we would consider that a challenge to those safety

14       systems.  And, of course, we know in this particular

15       case all of those safety systems functioned properly.

16            Q.   Okay.  And by one of the safety systems, that

17       was the plant operators manually tripping the plant off

18       when it reached 75 percent water level in the steam

19       generator, is that right?

20            A.   That's correct.  Our operators are trained to

21       anticipate an automatic safety system actuation, and

22       proactively initiate a manual actuation of that

23       particular safety system before the automatic system

24       would actuate.  That's sort of a redundancy, if you

25       will, in the training in the backup systems.

FLORIDA PUBLIC SERVICE COMMISSION

60

1            Q.   Now, in the testimony that was prefiled, which

2       you read earlier on Page 6, the question was what

3       extended the outage of Unit 4, and you referred to the

4       water level in the steam generators.  Here it says it

5       delayed the start up of both Turkey Point nuclear units,

6       does it not?

7            A.   It does.

8            Q.   Do you agree with that?

9            A.   No, I don't agree with that.  I went back and

10       looked at the schedules for the start up of both of

11       those units, and I think that, first of all, you have to

12       understand the context of these evaluations.  The

13       problem statements are framed rather broadly at the

14       initiation of one of these condition reports, which is

15       the parent document for this root cause evaluation, and

16       it would be an obvious leap to say that there was a

17       30-hour impact on the other unit.  But when I went back

18       and looked at how the schedules were sequenced and how

19       resources were reallocated, I personally could not get

20       to that conclusion.  So I think that that is a

21       speculative statement.

22            Q.   Okay.  On the cover page that I gave you, the

23       first page of the exhibit, Page 83, there are 16 members

24       that prepared this report, is that right?

25            A.   Sixteen members that participated in the

FLORIDA PUBLIC SERVICE COMMISSION

61

1       report.  Each of them has various levels of expertise.

2       There wouldn't have been necessarily 16 people sitting

3       around a table writing this report.  Each person would

4       have bits and pieces of this that they would typically

5       do.

6            Q.   And did you review this report when it was

7       issued?

8            A.   No.

9            Q.   Only as part of this case?

10            A.   As part of this procedure.

11            Q.   Okay.  Could you turn to the page that has an

12       86 at the bottom, and that's the staff exhibit

13       Bates-stamped 413.

14            A.   I'm there.  Page 6, did you say?

15            Q.   86 at the bottom.  It's about the fourth page

16       in.

17            A.   Okay, I have it.

18            Q.   And this is the executive summary of the root

19       cause analysis, is that right?

20            A.   Yes.

21            Q.   What does it mean by root cause?

22            A.   Root cause is where after a condition report

23       is initiated for an unexpected situation in the plant we

24       put together a cross-functional team, as you indicated

25       earlier, and we look at all of the possible causes and

FLORIDA PUBLIC SERVICE COMMISSION

62

1       we narrow that down to what we call contributing causes

2       and what we would call the root cause of the particular

3       event, in this case that being the 75 percent level in

4       the steam generator and attendant manual reactor trip.

5            Q.   And in this case you have both a root cause

6       and then several contributing causes, is that right?

7            A.   That's correct.

8            Q.   What was the root cause?

9            A.   The root cause, as indicated in the report,

10       was insufficient guidance for the initial loading of the

11       main generator and for stabilizing power by preparing to

12       transfer to automatic feed reg valve control.

13            Q.   Okay.  And you are reading from the paragraph

14       that is under the heading major conclusions of the root

15       cause effort, is that right?

16            A.   That is correct.

17            Q.   And just before that section you read it says

18       the procedure used in this evolution -- and it refers to

19       a document, I gather, 4-GOP31, hot standby to power

20       operation.  Do you see that?

21            A.   Yes, 4-GOP301, I believe, is the procedure in

22       question.

23            Q.   And is that a Florida Power and Light created

24       document?

25            A.   That's correct.

FLORIDA PUBLIC SERVICE COMMISSION

63

1            Q.   And it says that that document did not provide

2       sufficient guidance for the rate of initial loading of

3       the main generator, is that right?

4            A.   That's correct.  I think that perhaps a little

5       bit of context and explanation would be useful for some

6       in the room here.  This portion of a reactor startup at

7       lower power level, when you are transitioning from what

8       we call bypass feed water control to main feed water

9       control is a very critical and important evolution

10       obviously in the plant.

11                 And the manual -- the bypass feed water system

12       is not an automatic system.  That is a manual system.

13       So the goal that the operators have and the way they are

14       trained is to as quickly as possible, while maintaining

15       stability, to move through that low power region and get

16       up into a .12 to .15 percent power where you can

17       effectively transition off of these by-pass manual feed

18       water valves and get into what we call automatic feed

19       water control.  The plant is a lot more stable at that

20       point in time.

21                 So what you are doing, in essence, it is a

22       balancing act between moving as quickly as possible

23       through this region, if you will, while maintaining the

24       stability, recognizing that the longer time that you

25       spend in this power region the more opportunity you

FLORIDA PUBLIC SERVICE COMMISSION

64

1       present for a transient because you are in manual

2       control and you want to get into automatic control.

3                 So you are doing a balancing act, if that

4       makes sense, between moving as quickly as possible

5       versus loitering in that area.  And the stability of the

6       feed water system is highly dependent on a number of

7       variables, multiple variables that can change from

8       startup to startup, and so it is very, very difficult to

9       prescriptively put into an operating procedure precisely

10       how these operators should load that generator.  And so

11       the training that they have been given through the

12       years, and I think it has proven to be generally very

13       successful, is to have a good understanding of these

14       tradeoffs that you make and to give them as much

15       flexibility as possible on that loading of the

16       generator, dependent upon the plant systems.

17                 So, in this particular case, this was a very

18       experienced operator who did this evolution.  He had

19       done it in the past, so obviously that individual knows

20       how to do this successfully.  So it is typical -- not

21       just at our plants at FPL, but across the industry -- to

22       not try to write an overly specific criteria into these

23       procedures for that particular reason.

24            Q.   Let's talk a bit about what the operators did.

25       Could you turn to page what has a Bates-stamped 93 at

FLORIDA PUBLIC SERVICE COMMISSION

65

1       the bottom, which from the staff exhibit is Bates stamp

2       420?

3            A.   I'm there.

4            Q.   Okay.  And toward the bottom of the page there

5       is three items listed; A, B, C.  The first one is

6       prevention causal factor one.  Do you see that?

7            A.   Yes.

8            Q.   It states there that the turbine operator and

9       the SRO, and the SRO would be the senior reactor

10       operator?

11            A.   That's correct.

12            Q.   They continued to increase main generator load

13       while steam generator levels not stable, is that right?

14            A.   Yes.

15            Q.   I take it that's something they weren't

16       supposed to do?

17            A.   Well, I think putting myself in their shoes,

18       since I have been in that position in the past myself, I

19       believe at the time in the control room they felt as

20       though the steam generator levels were sufficiently

21       stable in order for them to continue to increase load.

22       It was only in hindsight after the event that you could

23       go back and look at the data and draw a conclusion that

24       perhaps we know because it resulted in a scram, or a

25       reactor trip that they could have let those levels

FLORIDA PUBLIC SERVICE COMMISSION

66

1       stabilize out a little bit longer.

2                 But at that point in time they knowingly moved

3       forward believing that they were, in fact, stable enough

4       to continue forward.  And that's based on their

5       experience.  As I indicated, that operator at the

6       controls had multiple start-ups on his resume.

7            Q.   Mr. Stall, you said that they felt it was

8       stable, but if you go down to number C, or the letter C,

9       it says the operator crew failed to stop, slow down when

10       unsure.  Do you see that?

11            A.   I see that.

12            Q.   Doesn't that say the operators were unsure and

13       they just kept going anyhow?

14            A.   I don't believe that the operators were

15       unsure.  As I indicated, these operators have started up

16       these units in the past.  They have a sense around when

17       it's stable enough or not stable enough in order to

18       continue to load the generator.  These operators at

19       Turkey Point have exhibited in many occasions that they

20       do know when to stop when they are unsure.  They would

21       not have knowingly proceeded in the face of an

22       instability that they didn't think was manageable to try

23       and attempt to put this unit on-line.  They believed at

24       that time that they were doing the right thing.

25                 Now, you know, it's pretty simple to look back

FLORIDA PUBLIC SERVICE COMMISSION

67

1       after the event and say, well, you know, you should have

2       recognized that these levels were perhaps oscillating a

3       little bit more than they might have under a different

4       circumstance, and maybe you were unsure and should have

5       stopped.  But I don't believe that for one moment that

6       they were unsure of themselves at that moment in time

7       and proceeded.  They are just not trained that way and

8       they wouldn't behave that way.

9            Q.   Mr. Stall, let me ask you to go back to the

10       page that has an 86 at the bottom, which is Bates

11       stamped 413 on the staff exhibit?

12            A.   I'm there.

13            Q.   Okay.  Now, we have already talked about the

14       root cause being insufficient guidance, is that right?

15            A.   Yes.

16            Q.   There is also a number of contributing causes

17       that were identified by this team, is that right?

18            A.   Yes.

19            Q.   One of them is the reactor control operator

20       did not attend just-in-time training, is that right?

21            A.   That's correct.

22            Q.   And how did that contribute to the shutdown?

23            A.   Well, obviously the preferred methodology for

24       doing just-in-time training would be that you would have

25       the exact same crew in the simulator practicing this as

FLORIDA PUBLIC SERVICE COMMISSION

68

1       will be in the control room for the actual startup.  But

2       because of the complex overtime rules by the NRC and

3       various other competing interests, that's not always

4       possible, and there is no regulatory requirement for

5       that to occur.  I think the most important thing to keep

6       in mind here is that all of those individuals who

7       practiced in the simulator and who performed that

8       startup in the control room are licensed reactor

9       operators by the Nuclear Regulatory Commission, so they

10       are fully qualified independent of this just-in-time

11       training to execute a plant start-up as in this

12       particular case.

13            Q.   A second contributing cause, Mr. Stall, and it

14       is the second bullet as we look down this page, was the

15       abnormally fast generating loading.  Do you see that?

16            A.   I do.

17            Q.   What does it mean by abnormally fast?

18            A.   Well, I think it means, in this particular

19       case, that the loading of the generator which is

20       influential on the steam generator level control system

21       was faster than had typically been done in the past, and

22       that that was a contributing cause to the transient that

23       resulted in the reactor trip.

24            Q.   Let me ask you about the third bullet.  It

25       says a weakness in the understanding of the

FLORIDA PUBLIC SERVICE COMMISSION

69

1       shrink-and-swell concept is a contributing cause.  Do

2       you see that?

3            A.   I do.

4            Q.   Could you tell us what the shrink-and-swell

5       concept is?

6            A.   This is a little bit complex, but let me see

7       if I can simplify this as much as possible.  The steam

8       generators are nothing but large heat exchangers, and

9       they are a tube and shell designed heat exchanger.  On

10       the tube side you have reactor coolant system water that

11       is at approximately 547 degrees.  And on the shell side

12       is the secondary system which takes the feed water,

13       turns it to steam, and powers the turbine.  And the way

14       the operators would load the generator is they control

15       the turbine load.  They'll demand the valves on the

16       turbine to come open to increase load, they will close

17       the valves on the turbine to decrease load.

18                 Shrink and swell refers to a physical

19       phenomenon that results from the movement of those

20       control valves as one variable.  And as I indicated

21       before, there are a number of other variables that can

22       influence that, as well, but for a moment we'll focus on

23       the control of the turbine valves.  As you begin to open

24       up these turbine valves, what you're doing is you're

25       drawing more steam off of the steam generator for the

FLORIDA PUBLIC SERVICE COMMISSION

70

1       turbine to increase the load.  And as you do that you

2       are, in essence, depressurizing the steam generator,

3       which will be somewhere around 1,000 to 1,100 pounds in

4       pressure.  As you depressurize that steam generator, the

5       level will swell.  And if you could think about this in

6       a simplified way, if you have ever opened a bottle of

7       Coca-Cola, for example, and you pop the top off, have

8       you ever noticed that sometimes the bubbles, and it'll

9       increase in level and sometimes even overflow the

10       bottle.  It's the same physical phenomena.  As you open

11       up these valves, the level will increase and that will

12       be swell.

13                 Now, the shrink side of that is a little bit

14       counterintuitive, as well.  If an operator opens up the

15       feed water valves and admits what we would cold feed

16       water to the steam generators, then the initial response

17       of the steam generators is when that cold feed water is

18       seen in the steam generator it will increase the density

19       actually in the steam generators of that water and it

20       will cause that water to shrink.  And then as that water

21       that's introduced to the steam generator picks up heat,

22       then you'll have a swell phenomenon.

23                 So I think the point that is important here

24       for everybody to understand is that, once again,

25       operating in this region is not the most stable region

FLORIDA PUBLIC SERVICE COMMISSION

71

1       to operate in.  And that's why our operators not just at

2       FPL but across the industry are trained to understand

3       the variables that influence this and to move as quickly

4       as they safely can through this region to get into

5       automatic feed water control.

6                 COMMISSIONER EDGAR:  Mr. Beck, I'm sorry, the

7       bullets that the witness is referring to that you are

8       asking about, what page are you on?

9                 MR. BECK:  The Bates stamp is 413 for the

10       staff exhibit, and there's a Florida Power and Light

11       Bates stamp of 86 at the bottom.

12                 COMMISSIONER EDGAR:  That's the one I wanted.

13       Thank you.

14                 And if I may, Commissioner Skop, what time did

15       you say you were planning that we take a lunch break?

16                 COMMISSIONER SKOP:  Depending on the will of

17       the Commission, I was thinking about 12:00 o'clock.

18                 COMMISSIONER EDGAR:  Okay.  Thank you.  I

19       appreciate it, Mr. Beck.

20            BY MR. BECK:

21            Q.   Mr. Stall, thank you for the explanation of

22       shrink and swell.  Is that a phenomena that your

23       operators are trained in and are supposed to be

24       knowledgable about?

25            A.   I think they are generally knowledgable about

FLORIDA PUBLIC SERVICE COMMISSION

72

1       that, but, of course, the degree of an in-depth

2       knowledge of that phenomenon, as in this case, it can

3       vary from one operator to another.  But I think we come

4       back to first principles, and that is that they are

5       trained to understand the variables that can influence

6       the level in the steam generators, and to try to balance

7       that loading of the generator as quickly as possible

8       with maintaining a stability and not causing a level

9       oscillation.

10            Q.   Let me ask you to turn to the page that has a

11       99 at the bottom, it's FPL 10-99.  It's also 426 in the

12       staff's exhibit.

13            A.   I'm there.

14            Q.   In about the middle of the page there is a

15       larger paragraph.  It says during the latter stages, and

16       I'd like to ask you about the sentence that is five

17       lines down where it states, "The significance of the

18       wide range level indicators is that shrink and swell

19       phenomena can be easily diagnosed by comparing the

20       narrow range level indicators to the wide range level

21       indicators."

22                 Could you explain what that's referring to?

23            A.   Certainly.  The mechanical design of the steam

24       generators is such that you have, as I indicated

25       earlier, you have got these tubes, it's a tube and shell

FLORIDA PUBLIC SERVICE COMMISSION

73

1       heat exchanger.  Tubes in the interior of the steam

2       generator that on the inside of those tubes is the

3       reactor coolant system water, which is the heat source

4       for the secondary water, which is the feed water.

5                 Surrounding the tube bundle is what we call a

6       wrapper, and you have several sets of level taps, as we

7       would call them, that are mechanically plumbed into the

8       steam generator.  One is the wide range level, which if

9       this bottle of water was the steam generator, the wide

10       range level taps would be on the outside of the steam

11       generator tap or the wrapper, and they would go from the

12       top basically to the bottom.

13            Q.   Okay.

14            A.   For example, the narrow range, which are

15       highly influenced by the hydrodynamics that are going on

16       in that region between the wrapper and the outer shell

17       are in the operating -- you know, much narrower in the

18       operating band.  And so I think what the author of this

19       document is trying to say, and I do agree with them, is

20       that looking at the wide range level can provide useful

21       intelligence about what the trends are going to be on

22       the behavior of the narrow range level.

23            Q.   Okay.  The author of this document down on the

24       next paragraph also indicates that the events described

25       in the preceding paragraphs indicate a fundamental

FLORIDA PUBLIC SERVICE COMMISSION

74

1       knowledge gap by some operators regarding

2       shrink-and-swell phenomena.  Would you agree with that?

3            A.   I would agree with that.  But, I think, again,

4       I'm going to have to come back to a broader point here

5       and that is that our training programs -- not just at

6       FPL, but in this industry -- constantly reveal gaps in

7       knowledge and training in operators.  And we use what is

8       called the systematic approach to training where we

9       consciously look for opportunities to identify training

10       gaps, put them back into our continuing training

11       program, share those with the industry, and learn from

12       those.

13                 I think it's important to realize that these

14       operators are really doing a herculean job out there,

15       and there are going to be particularly as we begin to

16       transition operators who are retiring out in with new

17       operators, there are going to be knowledge gaps going

18       forward that we are going to find.  And, yes, some of

19       those knowledge gaps are going to manifest themselves in

20       an event like this.  But I don't think that the standard

21       can be perfection, either.  I think that you have to

22       step back and look at the process from a broader point

23       of view and not focus in on every knowledge gap that

24       results in some deficiency, and say that, well, you

25       know, obviously these operators weren't well trained,

FLORIDA PUBLIC SERVICE COMMISSION

75

1       because we have demonstrated in the past the ability to

2       start these units up, and nobody is going to be perfect.

3       These events are going to happen from time to time, and

4       I don't think we should be holding these operators to

5       standards of perfection, which is what I feel like we

6       are doing in this particular case.

7            Q.   The shrink-and-swell phenomena is not a

8       phenomena that is unique to a nuclear plant, is it?

9            A.   I can't say that.  I don't believe that I can

10       answer that, but I would surmise that it is, in fact,

11       unique to a nuclear plant.  Yes, I would think it would

12       be.

13            Q.   Are there not steam generators -- isn't it

14       more connected to a steam generator rather than the

15       actual nuclear plant?

16            A.   The steam generator is part of the nuclear

17       plant.

18            Q.   But you have other steam generators, do you

19       not?

20            A.   Not in this sort of design, no.  Not at all.

21       This is a unique design applied to a pressurized water

22       reactor in the industry.  So I would say that that is --

23       you know, on second thought, I would say for the record,

24       yes, this is unique to the nuclear industry.  I have

25       never heard of it being a phenomenon in general

FLORIDA PUBLIC SERVICE COMMISSION

76

1       industry, because there is nothing similar that I'm

2       aware of of this design in general industry.

3            Q.   Okay.  Let's turn to the issue about the rod

4       position indicator.  And you address this on Page 4 of

5       your testimony, do you not?

6            A.   Give me one moment to get to that page.

7            Q.   Sure.

8            A.   Yes, you're correct.

9            Q.   Okay.  And you discovered an issue regarding

10       the rod position indication system during the October of

11       2007 startup after the planned refueling outage, is that

12       right?

13            A.   That's correct.

14            Q.   Would you describe what happened?

15            A.   During the power ascension process, we

16       observed that that particular analog rod position

17       indicator, I believe, was reading high.  Again, to

18       provide a little bit of explanation on this system,

19       there are 45 control rods associated with each Turkey

20       Point unit down there, and these control rods are

21       grouped into what we call banks.  And each individual

22       control rod has its own analog position indicator, which

23       is a meter that's in the control room to show that

24       position of that rod.  And the operators will be

25       generally continuously -- especially during a power

FLORIDA PUBLIC SERVICE COMMISSION

77

1       ascension process -- scanning these meters looking for

2       alignment among the rods in that particular bank.  And

3       in this particular case, this rod position indicator

4       failed high.  The rod itself was physically at the right

5       position in the reactor.  The indication failed high.

6       And we have a specification in our license documents

7       that says that if there is a difference in an indication

8       of plus or minus 12 steps from the demand position, then

9       we must declare that rod inoperable.  And so the

10       operator at the controls observed that.

11                 We declared that particular rod inoperable and

12       we were able to continue the power ascension.  Now, the

13       problem with this is that as long as there is only one

14       rod in a particular bank of control rods that is out of

15       service, we have alternate ways of determining its

16       position and we can continue to operate.  But if we were

17       to have a second rod fail in that particular bank, it

18       would be an immediate shutdown requirement from the

19       Nuclear Regulatory Commission.

20                 So our engineers developed a modification

21       package where we were able to alternately determine a

22       way to display the indication of that rod, what its

23       actual position was by capturing a voltage signal and

24       translating it to a recorder in the control room.  And

25       we approached the NRC and indicated to them that we

FLORIDA PUBLIC SERVICE COMMISSION

78

1       believed that we had developed a method that would allow

2       us to safely determine the position of that rod, and we

3       asked for an amendment to our license to continue to

4       operate.  And they approved that amendment, but we had

5       offered along the way, and they included it in the

6       license amendment, that at the next outage where we shut

7       the unit down that we would repair that particular rod

8       position indicator, which we would have done anyway

9       because we want these operators to have full indication

10       of all of their instruments.  And that next opportunity

11       was at the February 26th outage.

12            Q.   So you were required, then, to fix that at the

13       next outage, whether it was unplanned or a planned

14       outage, is that right?

15            A.   That's correct.

16            Q.   And because this was an unplanned outage, it

17       added incremental time to bringing the units back

18       on-line, did it not?

19            A.   In this particular case it added incremental

20       time to the outage to effect that repair.  But I think

21       in keeping with that vein of thought, I think it is also

22       important to realize that we would have had to repair

23       that rod position indicator at the next forced outage

24       that we would have had.  Now, we had a forced outage in

25       June as it turned out to do a turbine balance shot, and

FLORIDA PUBLIC SERVICE COMMISSION

79

1       at that point in time we would have done that repair on

2       that particular rod in June.

3            Q.   Would you have been required to have done it

4       in June?  Did the plant go down enough that it was

5       required to be done?

6            A.   By the legal requirements in our operating

7       license, we would not have been technically required.

8       But I can tell you, and I think our track record

9       strongly supports this, that we have a policy of

10       operating with regard to our regulator, in this case the

11       Nuclear Regulatory Commission, that we will not take

12       advantage of the letter of the law.  We will meet the

13       spirit of the law.  And had we came to that event in

14       June of 2008 and we still had that problem with the rod

15       position indication system, we would have shut the unit

16       down and fixed that problem.  And I think that I can

17       support that with several examples of where we have shut

18       these units down before we reach a regulatory

19       requirement.

20                 As a matter of fact, the June of 2008

21       shutdown, we weren't required to shut the unit down

22       either.  We were running with high vibrations on the

23       turbine.  We still had operating margin, but we elected

24       to shut it down before we got there.  So we would never

25       have taken advantage of the regulation in the manner

FLORIDA PUBLIC SERVICE COMMISSION

80

1       that is suggested by that question.

2            Q.   Other than the June outage, the next outage

3       for Turkey Point Unit 3 was the regularly scheduled

4       refueling outage, is that right?

5            A.   That's correct.

6            Q.   And had the repair been done during the

7       regularly scheduled refueling outage, it would not have

8       extended that refueling outage, would it?

9            A.   No, it would not have.

10            Q.   Okay.  So it was the fact that this was an

11       unplanned outage that it added incremental time to this

12       outage?

13            A.   In the February outage.  I think the other

14       thing, too, that's important to understand is that as

15       these units operate through their operating cycle,

16       equipment problems are going to occur.  And what we do

17       is we keep a list of work orders that we want to work

18       when a unit comes down because we want to -- if we have

19       the opportunity, we want to fix it to give us every

20       opportunity to operate successfully to the next

21       refueling outage.

22                 So because just we did not have any other

23       forced outages other than that June of 2008 outage, we

24       can't say conclusively that would have been the case in

25       this case because we did other work orders that we would

FLORIDA PUBLIC SERVICE COMMISSION

81

1       have still been running with, and with problems that

2       occur during the cycle, we could have very well found

3       ourselves in another forced outage.  So it would be too

4       speculative to suggest that we could have operated to

5       the next refueling cycle.

6                 MR. BECK:  Mr. Stall, thank you.  That's all I

7       have.

8                 COMMISSIONER SKOP:  Thank you.

9                 Ms. Bradley, you're recognized for

10       cross-examination.

11                 MS. BRADLEY:  Thank you.

12                          CROSS EXAMINATION

13            BY MS. BRADLEY:

14            Q.   Mr. Stall, you were talking with Mr. Beck at

15       Bates stamp 413 and the root cause analysis?

16            A.   On the steam generator level trip?

17            Q.   Yes, I believe that's correct.

18            A.   Yes.

19            Q.   Who prepared that document?

20            A.   There's a list of team members on the first

21       page there.  I believe that Mr. Beck referred to them.

22            Q.   Are those employees of Florida Power and

23       Light?

24            A.   That's correct.

25            Q.   Do you know who assigned them to prepare this

FLORIDA PUBLIC SERVICE COMMISSION

82

1       report?

2            A.   I don't know specifically by name, but it

3       would have been somebody in the plant management staff.

4            Q.   And was that person authorized by the company

5       to make this kind of team assignment?

6            A.   Yes.

7            Q.   The persons that did this, were they qualified

8       to perform that type of analysis and work?

9            A.   Yes.

10                 MS. BRADLEY:  No further questions.

11                 COMMISSIONER SKOP:  Thank you, Ms. Bradley.

12       Ms. Kaufman.

13                 MS. KAUFMAN:  Thank you.

14                          CROSS EXAMINATION

15            BY MS. KAUFMAN:

16            Q.   Good morning, Mr. Stall.  How are you doing?

17            A.   Good, thank you.

18            Q.   I just want to follow up on some questions

19       Mr. Beck asked you and Ms. Bradley.  Mr. Beck took you

20       through the root cause analysis that you still have in

21       front of you, and he asked you some questions about the

22       water level in Unit 4 that exceeded 75 percent.  Do you

23       recall that?

24            A.   That's correct.

25            Q.   And he took you through some of the root

FLORIDA PUBLIC SERVICE COMMISSION

83

1       causes and the contributory causes to that event.  Do

2       you recall that?

3            A.   Yes.

4            Q.   And the report that Ms. Bradley and Mr. Beck

5       asked you about identified, I think, what are called

6       some knowledge gaps and some other causes of the event.

7       Do you agree with that?

8            A.   I do.

9            Q.   Mr. Stall, would you also agree that

10       ratepayers don't have any ability to influence or change

11       some of these knowledge gaps or issues that FPL

12       employees may have?

13            A.   I would agree with that.

14            Q.   And that that sort of training and information

15       would be within the purview of FPL management practices?

16            A.   Yes.

17            Q.   Now, you would agree -- and I think we heard

18       this in the open statements, but you would agree,

19       wouldn't you, that the Turkey Point nuclear units came

20       off-line on February 28th, 2008, as a result of some

21       actions by FPL employees at the Flagami Substation?

22            A.   I believe the date was February 26th.

23            Q.   I'm sorry.  You're right, February 26, 2008.

24            A.   Correct.

25            Q.   Okay.  And you would agree that the reason the

FLORIDA PUBLIC SERVICE COMMISSION

84

1       units tripped were due to some actions of employees at

2       that substation?

3            A.   Correct.

4            Q.   Okay.  And if those actions or activities had

5       not occurred at the substation as far as you know that

6       Units 3 and 4 would have continued to run, is that

7       correct?

8            A.   On that particular day.  However, you know,

9       who knows what might have happened.  I mean, we can only

10       say that it certainly wouldn't have tripped from that

11       particular event.

12            Q.   Right.  You testify on Page 8 of your Direct

13       Testimony starting at Line 9 --

14            A.   On which line, I'm sorry?

15            Q.   The question begins at Line 9, but to

16       paraphrase, the question is did the NRC have any issues

17       arising out of the shutdown of the units, and you say

18       they did not, correct?

19            A.   Yes.  The NRC had no issues.  And as a matter

20       of fact, in their inspection reports they found that the

21       units were handled and restarted successfully without

22       error, I believe, is the word they had.

23            Q.   Does the NRC have any responsibility for

24       determining what replacement fuel costs might be for

25       Florida ratepayers?

FLORIDA PUBLIC SERVICE COMMISSION

85

1            A.   No.

2                 MS. KAUFMAN:  Thank you.  That's all I have.

3                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

4                 Staff.

5                 MR. YOUNG:  Thank you, sir.

6                          CROSS EXAMINATION

7            BY MR. YOUNG:

8            Q.   Good morning, Mr. Stall.  How are you?

9            A.   Good morning, Mr. Young.

10            Q.   All right.  You mentioned earlier that FPL

11       complies with work orders.  Do you remember that

12       statement?

13            A.   Excuse me?

14            Q.   You mentioned that FPL complies with work

15       orders for nuclear units, and when the opportunity

16       arises, FPL tries to perform these work orders.  Do you

17       remember that you stated that earlier?

18            A.   Yes.

19            Q.   Is this unique to nuclear units, or do you

20       also do this type of preparation for fossil fuel units?

21            A.   I don't have direct responsibility for our

22       fossil fleet, but I'm comfortable with saying that they

23       would do everything they can to be prepared for any

24       forced outage event, as well.  They run a very efficient

25       fleet.

FLORIDA PUBLIC SERVICE COMMISSION

86

1            Q.   Okay.  During cross-examination of Mr. Beck

2       you talked about the RPI system, correct?

3            A.   Yes.

4            Q.   All right.  Why didn't FPL perform the RPI

5       system repair when they initially discovered it in

6       October of 2007?

7            A.   Because we had come out of the refueling

8       outage, and as I indicated earlier, we had that one rod

9       position indication that had failed, so we were well

10       within our operating license guideline to continue to

11       operate the plant.  And we were able to develop an

12       alternate methodology for determining that particular

13       rod position that was safely executed and approved by

14       the Nuclear Regulatory Commission.

15            Q.   All right.  And that alternative allowed you

16       to operate until the next outage, correct, or the next

17       planned outage possibly, next planned outage, correct?

18            A.   Either the next forced outage or the next

19       planned outage, whichever occurred first.

20            Q.   Do you recall how long it was after the

21       Flagami transmission event that FPL began working on

22       those repairs?

23            A.   I would have to go back to the work order for

24       the exact time, but there would not have been the

25       ability to get into that reactor compartment immediately

FLORIDA PUBLIC SERVICE COMMISSION

87

1       after the shutdown to begin those repairs.  I'm

2       confident from looking at the background material that

3       they got on top of that job as quickly as possible.  You

4       have to realize that it's very hot in there, a difficult

5       environment.  Radiation surveys have to be performed,

6       radiation work permits have to be written, so there is a

7       time delay between the moment that that reactor trip

8       breaker opens and the plant comes down and when that

9       crew is dispatched to actually go do the physical work.

10       There are a lot of administrative and safety precautions

11       that must be taken.

12            Q.   So would you agree, subject to check, it was

13       approximately seven to eight hours after the Flagami

14       transmission event that FPL began work on those repairs?

15            A.   I would have to look at the documents, but I

16       think that would be reasonable.

17            Q.   Okay.  Now, prior to or since that initial

18       discovery of the RPI system in October 2007, has FPL

19       experienced issues with the RPI system at Turkey

20       Point's -- either Turkey Points 3 or 4?

21            A.   Yes.  We had had some issues with the rod

22       position indication system on both Unit 3 and Unit 4

23       prior to that point in time.

24            Q.   Okay.  Now, you discussed the issues which

25       delayed the return of Unit 4.  Do you remember that

FLORIDA PUBLIC SERVICE COMMISSION

88

1       discussion?

2            A.   With regard to the steam generator level

3       transient, yes.

4            Q.   Now, in your response to Staff's Interrogatory

5       Number 13, and that's Bates stamp Number 256, and if you

6       look on -- Commissioners, if you look on the computer

7       it's the Hearing Exhibit Number 27 on the CD, and it's

8       in the first file.

9            A.   I'm trying to find it here.  Could you direct

10       me to it one more time?

11            Q.   It's Staff's Response to Interrogatory Number

12       13.  It's Bates stamp Number 256.

13            A.   I have it, I believe.

14            Q.   And just to speed things up, you indicated in

15       this response that FPL commenced startup of Turkey Point

16       Unit 4 on February 28th, 2008, at 4:58 a.m., is that

17       correct?

18            A.   Yes.

19            Q.   Absent the issues with the delay and the

20       shutdown due to high steam generator, at what time did

21       you believe Unit 4 would have returned on-line given the

22       consideration in your response to Interrogatory Number

23       13?

24            A.   Shortly after 0458.  I think that's when we

25       had the -- let's see.  I'd have to go back and look at

FLORIDA PUBLIC SERVICE COMMISSION

89

1       the timeline, but I see that we commenced startup at

2       Unit 4 on February 28th at 0458, and then he had the

3       high steam generator water level event on February 29th

4       at 0450.  So we had a period of time there between the

5       commencement of that startup and when we had that level

6       transient.

7            Q.   Okay.  Now, earlier I think it was with Mr.

8       Beck or Ms. Kaufman, you talked about the RPI in terms

9       of the NRC's statement in terms of you repairing the RPI

10       system during the next planned shutdown, correct?

11            A.   Yes.

12            Q.   Or the next shutdown.  Did FPL consider taking

13       down the plants to repair the RPI system?

14            A.   Well, as I indicated in my testimony -- not

15       testimony, but deposition, excuse me, earlier, I

16       considered, in the back of my mind, looking for an

17       opportunity before the hot summer months to proactively

18       take the unit down and fix this problem.  But as you and

19       I had spoken in the deposition, there is no

20       documentation to that effect.

21                 COMMISSIONER SKOP:  Mr. Young, can we take a

22       quick five-minute break here to allow the court

23       reporters to switch out.  It looks like they are trying

24       to do that, so let's stand adjourned here as a stopping

25       point for five minutes.

FLORIDA PUBLIC SERVICE COMMISSION

90

1                 MR. YOUNG:  Yes, sir.

2                 (Recess taken.)

3                 COMMISSIONER SKOP:  Okay.  We're going to go

4       back on the record.  And, staff, you're recognized for

5       cross-examination.

6                 MR. YOUNG:  Staff has no further questions.

7                 COMMISSIONER SKOP:  Thank you.

8                 Commissioners?

9                 COMMISSIONER EDGAR:  I do.

10                 COMMISSIONER SKOP:  Commissioner Edgar.

11                 COMMISSIONER EDGAR:  Thank you.

12                 Mr. Beck, this document that you were using

13       for some of your cross labeled Turkey Point Nuclear

14       Plant Steam Generator Level Manual Trip, has this -- is

15       this marked as an exhibit?

16                 MR. BECK:  No, Commissioner, because it's part

17       of the staff exhibit that's already been admitted into

18       evidence.

19                 COMMISSIONER EDGAR:  Wonderful.  Thank you.

20                 I have one question for the witness using,

21       referencing this document that Mr. Beck was asking you

22       about.  On the page that says Page 17 of 72, and at the

23       top it is the beginning of the section on Causal Factor

24       3.

25                 THE WITNESS:  Okay.  I find it.

FLORIDA PUBLIC SERVICE COMMISSION

91

1                 COMMISSIONER EDGAR:  Okay.  Towards the bottom

2       it talks about an operator not having a peer checker as

3       is recommended in some recommendation type document.

4       I'm not sure what that is referring to, NAP 402.  Could

5       you describe to me this process and requirements of a

6       peer checker, and if in your opinion where it says that

7       there was not a peer checker, what the importance of

8       that is or is not?

9                 THE WITNESS:  Okay.  Peer checking is a

10       technique that has been developed in the industry.  It

11       is primarily an error minimization tool, and it is not a

12       regulatory required process by the Nuclear Regulatory

13       Commission but one that we adopt in order to again

14       minimize potential for errors.  And the way it is used

15       is that there are certain evolutions that are performed

16       both in the control room and out in the plant proper

17       that have the potential for a problem to result if they

18       are not performed correctly, and so we, we assign

19       individuals to perform what we would call peer checks.

20                 For example, if I was going to be starting a,

21       a critical pump, I would want to obviously make sure

22       that I'm on the right pump.  There's plenty -- there's

23       hundreds of pumps in the control room.  Before I start

24       that pump, I want to make sure I'm on the right pump,

25       for example.  So I would go to that particular switch

FLORIDA PUBLIC SERVICE COMMISSION

92

1       and I would say I'm preparing to start 1FWP1 Alpha, main

2       feedwater pump.  And if you were the peer checker, you

3       would basically stand right next to me and say I

4       understand you are preparing to start 1FWP1 Alpha, that

5       is the correct switch, and then I would start it.  And

6       we would both look at the response of the system and

7       concur that we had the expected response.

8                 During this period of time again that we're

9       talking about with this startup of the unit there are a

10       lot of critical activities going on, so there is a lot

11       of peer checking activity going on as well.  And I think

12       what this gets to is that in this particular case peer

13       checking was going on of something that was deemed to be

14       perhaps of higher significance than this particular item

15       that's talked about, and so it was not peer checked.

16                 COMMISSIONER EDGAR:  So in your, your opinion,

17       in your expertise and your knowledge of this document,

18       realizing as you've just said that there would have been

19       a lot going on at the same time, is the point made on

20       this page that a peer checker was not utilized at this

21       point, is that significant or not significant?

22                 THE WITNESS:  I don't, I don't believe it is

23       significant in this particular point because, again, the

24       operator at the controls was a veteran operator who had

25       conducted multiple startups successfully in the past,

FLORIDA PUBLIC SERVICE COMMISSION

93

1       and there were other more critical things going on at

2       that point in time that caused the unit supervisor to

3       perhaps be peer checking something else.  And as we

4       talked about earlier, that operator at the controls

5       believed that he had those steam generator level

6       oscillations under, under control at that point in time.

7                 COMMISSIONER EDGAR:  All right.  Thank you.

8       Thank you.

9                 THE WITNESS:  You're welcome.

10                 COMMISSIONER SKOP:  Thank you, Commissioner.

11                 Commissioner Klement, I believe you had a

12       question, then Commissioner Stevens.

13                 COMMISSIONER KLEMENT:  Thank you, Mr.

14       Chairman.

15                 Mr. Stall, I would like to refer to the, your

16       test, your statement on Page 4, the question on Line 22,

17       "Could FPL have restarted Unit 3 without repairing the

18       affected RPI system?"  And your answer from Line 1 to 7

19       is "No."  And you say that the NRC required you to do

20       the rod replacements at the next shutdown downtime.  Yet

21       I think, I thought I heard you say just before, a few

22       minutes before the recess, the last recess, that you

23       were not actually required to shut it down, but in the

24       spirit of the law as well as the letter, you chose to do

25       so.  Is -- am I hearing right or --

FLORIDA PUBLIC SERVICE COMMISSION

94

1                 THE WITNESS:  No.  What I was -- let me --

2       perhaps I wasn't speaking clearly, so let me attempt to

3       elucidate that a little bit clearer for your benefit.

4                 What I was indicating was that we had a legal

5       requirement in place that if the unit was to shut down

6       for any reason at all, whether it was a forced outage or

7       a planned outage, following the issuance of that license

8       amendment, that we were required by law to repair that

9       particular rod position indication.

10                 And I believe the line of questioning at that

11       point in time was around had we not had the Flagami

12       transmission event, would we have had to complete that

13       repair when we had a subsequent outage in June of 2008?

14       And the point that I think was being made was that that

15       particular outage in June of 2008 was what we call a

16       Mode 2 outage, which meant that we kept the reactor

17       critical.  And so by the legal definition or requirement

18       in our operating license, we would not have been

19       technically required to execute that repair.  And then

20       we operated from June to the next refueling outage.  And

21       if we had gotten to the refueling outage, it would have

22       happened in the normal context of business.

23                 But my point that I was trying to make and

24       perhaps I wasn't very clear was that our policy is, is

25       to not -- it basically boils down to doing the right

FLORIDA PUBLIC SERVICE COMMISSION

95

1       thing.  And in this particular case it's not to take

2       advantage of the letter of the law with regard to how we

3       run our nuclear plants.  We -- and in June, for example,

4       when we shut that unit down with high vibrations on the

5       exciter bearing, we were still, had some operating

6       margin to the limit.  But we, we could see that it was

7       not an optimal condition, and so we shut the plant down

8       to do that repair before it drove us off of line.

9                 And so my point was, was that had we come to

10       that June situation where we were going to shut down to

11       do this turbine vibration shot and if that rod position

12       indication was still a problem because Flagami had not

13       occurred, we would have certainly shut the unit down and

14       fixed it at that time because that is the right thing to

15       do and, you know, to preserve all indications for the

16       operator.  That's what our processes and our training

17       drives us to do.

18                 COMMISSIONER KLEMENT:  Thank you.  When was,

19       when was the next fuel, refueling downtime scheduled?

20                 THE WITNESS:  That would have been in, I

21       believe, March of 2009.

22                 COMMISSIONER KLEMENT:  Okay.  Thank you.

23                 THE WITNESS:  You're welcome.

24                 COMMISSIONER SKOP:  Commissioner Stevens.

25                 COMMISSIONER STEVENS:  Thank you, Mr. Chair.

FLORIDA PUBLIC SERVICE COMMISSION

96

1                 Mr. Stall, how many hours were the plants

2       down, Unit 3 and Unit 4?

3                 THE WITNESS:  Unit 4, I believe, was down for

4       158 hours and Unit 3 for 107 hours, I believe.

5                 COMMISSIONER STEVENS:  I think you have it

6       backwards, but that's, that's fine, according to the --

7                 THE WITNESS:  Yes.  I had it backwards.

8       Excuse me.  You're correct.

9                 COMMISSIONER STEVENS:  Okay.  How many hours

10       were customers without power?

11                 THE WITNESS:  I cannot say.  That would not

12       have been in my scope of responsibility, Commissioner.

13       I was solely focused on, on the operating, you know, the

14       reactors.  And the amount of time the customers were

15       without power was not something that I was particularly

16       focused on at that point in time.

17                 COMMISSIONER STEVENS:  Thank you.

18                 THE WITNESS:  You're welcome.

19                 COMMISSIONER SKOP:  Thank you.  Any further

20       questions?

21                 I have one.  Good morning, Mr. Stall.

22                 THE WITNESS:  Good morning, Commissioner Skop.

23                 COMMISSIONER SKOP:  I just wanted to focus on

24       the discussion regarding the Unit 4.  And on Page 412 of

25       the exhibit -- or Bates Number 412 that Mr. Beck had

FLORIDA PUBLIC SERVICE COMMISSION

97

1       asked you about, there was a manual reactor trip as a

2       result of the steam generator level.  And as part of the

3       problem statement in the second paragraph it states,

4       "This manual reactor trip challenged plant systems and

5       caused financial consequences by adding an unplanned

6       unit cycle and delaying startup on both Turkey Point

7       nuclear units by approximately 30 hours."  Can you

8       briefly explain, if that statement is accurate, why it

9       would cause a delay in the startup of both units?

10                 THE WITNESS:  Well, I think, as we, as we

11       talked about earlier, I think, first of all, these

12       problem statements are developed immediately after the

13       event and they're typically written in a very broad sort

14       of way to encompass any particular outcome that may, you

15       know, end up in the ultimate root cause of it.

16                 But essentially what is going on is that again

17       you have, you have two units that are out of service

18       simultaneously and you have a fixed number of resources

19       available.  And as you'll focus on one unit being what

20       we would call the lead unit and the other unit being the

21       lag unit in terms of returning of the service, in this

22       particular case Unit 4 would have been the lead unit for

23       restart because we knew we had this rod position

24       indication system repair to do on Unit 3.

25                 So when we had the steam generator water level

FLORIDA PUBLIC SERVICE COMMISSION

98

1       transient that resulted in a manual reactor trip, then

2       we're, we're going to divert resources, we're going to

3       take a look and step back and say, okay, now which unit

4       is more, was more further along in terms of being able

5       to recover?  And we'll adjust our resources for that to

6       make sure that we're getting the first unit back as

7       quickly as possible.  Because it's quite possible that

8       now Unit 3 might have become the lead unit.

9                 And that's why I said that I believed that

10       this problem statement when it was initially formulated

11       at the, at the beginning of when this analysis was

12       kicked off was overly broad and simplistic because it's

13       not a simple matter of saying there was a, there was a

14       delay of 30 hours on one unit and that translated to a

15       delay of 30 hours on the other unit.  That's not the way

16       that we would operate our business.

17                 COMMISSIONER SKOP:  Okay.  And I'm taking this

18       as 30 hours combined between, or 30-hour additional

19       delay.

20                 But with respect to your testimony, am I

21       correct to understand, and this is why I'm focusing on

22       Unit 4, am I correct to understand that Unit 3 could not

23       be immediately placed back in service and that's why it

24       had to be the lag unit because of the replacement of the

25       control rod indicator?

FLORIDA PUBLIC SERVICE COMMISSION

99

1                 THE WITNESS:  That's correct.

2                 COMMISSIONER SKOP:  Okay.  And that's pursuant

3       to a commitment that FPL made to the Nuclear Regulatory

4       Commission; is that correct?

5                 THE WITNESS:  Yes, sir.

6                 COMMISSIONER SKOP:  Okay.  All right.

7       Focusing on Unit 4 on Page, Bates Number 413, one of the

8       contributing causes was obviously the abnormal fast

9       generator loading, and it indicated that the unit

10       immediately, that load was immediately increased after

11       synchronization.  So would it be correct to understand

12       that the turbine generator was on the governor valve at

13       that point in time that load was being added?

14                 THE WITNESS:  Yes.  The way that the generator

15       is typically, in the loading of the turbine is

16       sequenced, you're typically on what we call throttle

17       valve control until about 1,700 RPM, and then you make a

18       swap between throttle valve to governor valve control.

19       So you are correct, we would have been on governor valve

20       control.

21                 COMMISSIONER SKOP:  Okay.  So as the loading

22       of the generator continued, obviously that would have,

23       the governor valve would have responded by opening, you

24       know, additional valves or the distance, additional

25       steam flow so you could meet load.  And as a result of

FLORIDA PUBLIC SERVICE COMMISSION

100

1       the lack of coordination between the feedwater and the

2       steam generator levels, that caused the manual reactor

3       trip.

4                 THE WITNESS:  That's one of the influences on

5       it, as well as reactor coolant system temperature,

6       pressure in the secondary site of the steam generator,

7       whether or not the feedwater heaters are fully in

8       service or partially in service.

9                 As I, as I mentioned earlier, and I think you

10       probably are aware from your experience as well, is that

11       there are a large number of variables that influence

12       this, and that, that is why I was trying to make the

13       point earlier that trying to be overly prescriptive in

14       an operating procedure, a one-size-fits-all approach to

15       the startups is, is not necessarily the proper way to go

16       about this.

17                 It's really all about understanding the

18       tradeoffs between being in manual control for longer as

19       you move slower through that region versus moving in a

20       safe but expedited manner to get into automatic control,

21       and no two startups will be the same.

22                 COMMISSIONER SKOP:  Okay.  With respect to

23       startups, how many times would you say that Unit 4 has

24       been started up since it's been placed in service just

25       generally?  A hundred, hundreds?

FLORIDA PUBLIC SERVICE COMMISSION

101

1                 THE WITNESS:  That's as good of an estimate as

2       any.  Many times.

3                 COMMISSIONER SKOP:  Okay.  How many times has

4       this specific type of transient event occurred at

5       startup?

6                 THE WITNESS:  One other time at Turkey Point

7       this has occurred, and we've had a couple of events at

8       St. Lucie.  But in the industry there have been

9       literally hundreds of these events.  And I think to my

10       point earlier, it's a testament to the overall training

11       and skills of our operators that we've been successful

12       as many times as we have.  And that's why it was

13       disturbing to me that we would now begin to, to say

14       that, well, the, you know, once in a blue moon an event

15       like this happens and therefore there's some inadequate

16       training or some culpability by our operators and

17       therefore we ought to be penalized.  Because to me

18       that's, that's asking for a standard of perfection,

19       which we're never going to rise to that standard.

20                 COMMISSIONER SKOP:  Okay.  And with respect to

21       your response, you indicated that there was one previous

22       instance where this specific type of transient event

23       occurred, and obviously there would have been corrective

24       action at that time put in place; is that correct?

25                 THE WITNESS:  That's correct.  As you're

FLORIDA PUBLIC SERVICE COMMISSION

102

1       probably well aware from your experience as well, that

2       our training and our -- the whole systematic approach to

3       training that we use in the industry is an extremely

4       self-critical approach where we -- if we have an

5       equipment problem, we go after every contributing and

6       potential cause for that.  We do the same on a, on a

7       human problem like we had with the steam generator level

8       control.  We look for gaps in training and knowledge and

9       we feed those back into our training programs to improve

10       the performance.  And I think that's one of the primary

11       reasons why the customers have benefited from these

12       plants performing significantly above industry average,

13       because of this self-critical approach that we take at

14       FPL.

15                 COMMISSIONER SKOP:  Okay.  And with respect to

16       this event in question, corrective action was put in

17       place to prevent reoccurrence; is that correct?

18                 THE WITNESS:  Yes, sir.

19                 COMMISSIONER SKOP:  Okay.  Now was that

20       corrective action separate and distinct from the prior

21       corrective action?

22                 THE WITNESS:  Yes, it was.

23                 COMMISSIONER SKOP:  Okay.  All right.  Great.

24       And just one final question:  With respect to the delay

25       in restarting the unit or bringing Unit 4 back online,

FLORIDA PUBLIC SERVICE COMMISSION

103

1       could that have been avoidable through improved operator

2       communication?

3                 THE WITNESS:  I don't, sitting here today I

4       cannot say with certainty that it could have been

5       avoidable.  It's possible that it could have been.  But

6       I believe again that at that point in time, having been

7       in those operator's shoes, knowing the way that they're

8       trained and their approach to operations, that

9       individual that feedwater controls on that particular

10       day believed with all of his heart that that plant was

11       stable enough for him to increase the load on the, on

12       the generator.

13                 And having been the experienced operator who

14       has done this successfully, I think that if, if that was

15       the position he took, even had he communicated with, on

16       this specific point with some of his peers, that they

17       could have very well came to the same conclusion that he

18       did, that, yes, I think that, you know, we're stable

19       enough to continue to increase power.

20                 COMMISSIONER SKOP:  Okay.  Thank you.

21                 THE WITNESS:  You're welcome.

22                 COMMISSIONER SKOP:  Yes.  Commissioner

23       Klement, you're recognized.

24                 COMMISSIONER KLEMENT:  One other question for

25       Mr. Stall, which is just following up on what, the one I

FLORIDA PUBLIC SERVICE COMMISSION

104

1       asked earlier.

2                 I'm not sure what your communication process

3       is with the NRC, but just, would it have been possible

4       when, in the early hours of this when you were making

5       these decisions about the rod replacement in connection

6       with the downtime to ask, to get on the phone or some

7       other way of communicating and ask them if you could be

8       excused from this requirement and delay it until your

9       scheduled outage to avoid having to replace this, this

10       power at the higher cost and thus saving, saving the,

11       the additional cost?

12                 THE WITNESS:  No.  That wouldn't have been

13       possible.  And the way that the, the Nuclear Regulatory

14       Commission operates is they turn essentially a blind eye

15       to the economic impact.  Their focus is solely on, on

16       safety, and we had previously made that commitment to

17       them.  And we would not have been able to go back and

18       ask in this particular case to extend that.  It just

19       wouldn't have been feasible.

20                 COMMISSIONER KLEMENT:  Okay.  Thank you.

21       That's all.

22                 THE WITNESS:  You're welcome.

23                 COMMISSIONER SKOP:  Thank you.  Any other

24       questions for Witness Stall?  Hearing none, if we can

25       take up exhibits.

FLORIDA PUBLIC SERVICE COMMISSION

105

1                 MR. ROSS:  Mr. Chairman, I do have some brief

2       redirect.

3                 COMMISSIONER SKOP:  Excuse me.  I stand

4       corrected.  We will turn to FPL for redirect.

5                 MR. ROSS:  Thank you.  Thank you, Mr.

6       Chairman.

7                         REDIRECT EXAMINATION

8       BY MR. ROSS:

9            Q.   Mr. Stall, you were asked a question by

10       Mr. Young about why the company didn't affect the repair

11       to the rod position indicator when it, when the problem

12       was discovered in October of 2007.  Do you remember that

13       question?

14            A.   I do.

15            Q.   If, if FPL had decided to shut the plant down

16       and to make the repair at that time, how long would that

17       repair have taken compared with how long it took after

18       the Flagami event?

19            A.   Well, I think that's the unfortunate part of

20       the discussion that we're having today.  We know that it

21       took approximately 127 hours to execute this repair

22       during the Flagami transmission event.  And by taking

23       the course of action that we did when that problem

24       revealed itself, and by that I mean going to the Nuclear

25       Regulatory Commission and proposing an alternate

FLORIDA PUBLIC SERVICE COMMISSION

106

1       methodology for ascertaining the position of that

2       particular rod, that gave us time to procure spare

3       parts, to plan the work order packages, to be ready to

4       go, as Mr. Young indicated, within eight hours of the

5       shutdown of that unit.  So we were able to minimize the

6       amount of time and impact on the customers.

7                 Had we elected to shut the unit down upon

8       receipt of that problem in October, it would have taken

9       a much longer period of time to execute that repair.  We

10       would not have had the parts available, we would not

11       have had the work order package fully planned, we

12       wouldn't have had necessarily the right people who are

13       qualified in that area available, and unfortunately I

14       don't think we would be talking about this here today.

15            Q.   You were asked a number of questions about the

16       root cause analysis on the manual reactor shutdown of

17       Unit 4 on high steam generator water level.  Can you

18       describe what the purpose of root cause analysis are as

19       used by FPL and the nuclear industry?

20            A.   A root cause analysis is, is a technique that

21       is used for a specific subset of conditions or problems

22       that occur in a plant.  I think it's important to

23       realize that anything that happens at one of these

24       nuclear plants that is, quote, out of the norm, we write

25       a, what we call a condition report.  We document that

FLORIDA PUBLIC SERVICE COMMISSION

107

1       problem, we put it into our system, and we, we treat

2       that condition report in one of several different ways.

3                 On the one hand, it can be a simple what we

4       call broke fix, a piece of equipment that is not

5       consequential to safety or generation failed, simply

6       repair it, fix it, put it back in service.  If it's a

7       little more significant, we can perform what is called

8       an apparent cause where we devote some resources to

9       getting to the, to the root of the problem.  But the

10       magnitude of resources that would need to be devoted to

11       do a full root cause are not warranted because the

12       significance of the problem didn't rise to a high enough

13       level.  The third level is what's called a root cause

14       where we invest a large number of resources, as we

15       talked about in this particular case, to get to the root

16       of the problem and its contributing causes.

17                 We write on the, we write literally tens of

18       thousands of these condition reports at any particular

19       site like Turkey Point in a year.  So there's a constant

20       volume going through the system, and we'll be doing on

21       average hundreds of root causes in a year.  So these

22       things are not out of the ordinary.  And it is not out

23       of the ordinary for something to be in a root cause,

24       particularly in a problem statement which is broad and

25       sweeping, that is not necessarily borne out later on

FLORIDA PUBLIC SERVICE COMMISSION

108

1       when the root cause is, is finished.  And there may be

2       conclusions that are reached in a particular root cause

3       that upon reexamination some people might have a

4       different opinion about.

5            Q.   You were asked some questions about the

6       generator loading rate in connection with the, the Unit

7       4 manual reactor shutdown and the speed of the loading

8       rate.  Is there any risks with going too slow as opposed

9       to going too fast?

10            A.   Yes.  As I attempted to explain earlier, it is

11       a tradeoff between moving expeditiously through this low

12       power region to get off of what we call manual feedwater

13       control where the vulnerability to a reactor trip is

14       much higher than once you're on main feedwater control

15       with the valves controlling automatically without

16       operator action.  So the operators are trained to move

17       through that low power region as quickly and safely as

18       possible while maintaining stable control to get into

19       that automatic control.

20                 The slower you go, the more time you spend on

21       manual feedwater control, the higher the probability

22       that you're going to have a reactor trip because you're

23       on manual control.  So it's a tradeoff.  And that's why

24       I said earlier that reducing these requirements to a

25       prescriptive step in a procedure is virtually impossible

FLORIDA PUBLIC SERVICE COMMISSION

109

1       to do and it can have perverse consequences of causing a

2       problem.  So that's why we try to give them as much

3       broad leeway in establishing that generator loading rate

4       as reasonably is possible.

5            Q.   With respect to the performance of the plant

6       in response to the Flagami event and the reactor trip

7       that we were talking about as well as the RPI repairs,

8       at any time was there ever any threat to plant personnel

9       or to the health and safety of the public?

10            A.   Absolutely not.  Safety is, is the most

11       important thing that we deal with, the health and safety

12       of the public.  And in no, no case was the health and

13       safety of the public jeopardized by this particular

14       event.  And that was confirmed by the Nuclear Regulatory

15       Commission's inspection of that dual unit outage and how

16       it was conducted at Turkey Point.

17                 MR. ROSS:  No further questions, Mr. Chairman.

18                 COMMISSIONER SKOP:  Thank you.  We'll take up

19       the exhibits at this point.

20                 MR. ROSS:  Mr. Stall is not sponsoring any

21       exhibits, Mr. Chairman.

22                 COMMISSIONER SKOP:  All right.  Great.

23                 Commissioners, it's after 12:00.  I just

24       wanted to see what the will of the Commission would be

25       in terms of lunch.  I was thinking, you know --

FLORIDA PUBLIC SERVICE COMMISSION

110

1                 COMMISSIONER STEVENS:  1:15.

2                 COMMISSIONER SKOP:  -- 1:15, 1:30.  Okay.  All

3       right.  Why don't we do this, why don't we reconvene at

4       1:30, and we stand adjourned for lunch.

5                 (Lunch recess taken.)

6                 COMMISSIONER SKOP:  Okay.  We're going to go

7       back on the record.  Where we had left off is Witness

8       Stall had finished his direct testimony and will return

9       for rebuttal later in the proceeding.  So, Mr. Butler,

10       if you'd call your next witness.

11                 MR. BUTLER:  Thank you, Commissioner Skop.  I

12       would call Mr. Gerald (sic.) Yupp, and Mr. Yupp has been

13       previously sworn.

14                 COMMISSIONER SKOP:  Thank you.

15                            GERARD J. YUPP

16       was called as a witness on behalf of Florida Power &

17       Light Company and, having been duly sworn, testified as

18       follows:

19                          DIRECT EXAMINATION

20       BY MR. BUTLER:

21            Q.   Would you please state your name and business

22       address for the record, Mr. Yupp?

23            A.   Gerard J. Yupp, 700 Universe Boulevard, North

24       Palm Beach, Florida.

25            Q.   By whom are you employed and in what capacity?

FLORIDA PUBLIC SERVICE COMMISSION

111

1            A.   I'm employed by Florida Power & Light as

2       Senior Director of Wholesale Operations in the Energy

3       Marketing and Trading Division.

4            Q.   Did you prepare and cause to be filed seven

5       pages of prefiled direct testimony in this proceeding on

6       January 13, 2010?

7            A.   I did.

8            Q.   Do you have any changes or corrections to make

9       to your prefiled direct testimony?

10            A.   I do not.

11            Q.   Okay.  If I asked you -- excuse me -- asked

12       you the questions contained in your prefiled direct

13       testimony, would your answers be the same?

14            A.   They would.

15                 MR. BUTLER:  Commissioner Skop, FPL asks that

16       the prefiled direct testimony of Gerard J. Yupp be

17       inserted into the record as though read.

18                 COMMISSIONER SKOP:  Very well.  The prefiled

19       testimony of the witness will be entered into the record

20       as though read.

21                 MR. BUTLER:  Thank you.

22       BY MR. BUTLER:

23            Q.   Mr. Yupp, are you also sponsoring Exhibits

24       GJY-1 through GJY-9, which are attached to your prefiled

25       testimony?

FLORIDA PUBLIC SERVICE COMMISSION

112

1            A.   Yes, I am.

2            Q.   And were those prepared by you or under your

3       direction, supervision and control?

4            A.   Yes, they were.

5                 MR. BUTLER:  Okay.  Commissioner Skop, I would

6       note that those exhibits, GJY-1 through 9, have been

7       prefiled or premarked as Exhibits 2 through 10 in the

8       Comprehensive Exhibit List.

9                 COMMISSIONER SKOP:  Thank you.

10                 (Exhibits 2 through 10 marked for

11       identification.)

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

120

1       BY MR. BUTLER:

2            Q.   And with that, Mr. Yupp, would you please

3       summarize your direct testimony?

4            A.   Good afternoon, Commissioners.  My direct

5       testimony in this docket provides FPL's calculation of

6       replacement power costs for the Flagami transmission

7       event that occurred on February 26th, 2008.  The direct

8       testimonies of FPL Witnesses Stall and Avera provide the

9       support and rationale for the methodology that FPL has

10       used for that calculation.

11                 The replacement power cost calculation

12       reflects costs associated with replacement fuel and

13       purchased power that was required to offset the loss of

14       generation after the Flagami event.

15                 The calculation was, was completed basically

16       in the following manner.  First, we totaled the fuel

17       cost for all the megawatt hours of additional generation

18       that was brought online in the first eight hours

19       immediately following the transmission event, and we

20       coupled that with the payments for the purchased power

21       that we purchased during that same time period

22       immediately following the event.

23                 From that we subtracted the value of the same

24       number of megawatt hours at FPL's system average cost

25       for the month of February.  The calculation resulted in

FLORIDA PUBLIC SERVICE COMMISSION

121

1       a replacement power cost total of just slightly over

2       $2 million, $2,024,035.  And that concludes my summary.

3                 MR. BUTLER:  Thank you, Mr. Yupp.  I tender

4       the witness for cross-examination.

5                 COMMISSIONER SKOP:  Very well.  Thank you.

6                 Mr. Beck, you're recognized on behalf of

7       Public Counsel for cross-examination.

8                 MR. BECK:  Thank you, Commissioner.

9                          CROSS EXAMINATION

10       BY MR. BECK:

11            Q.   Good afternoon, Mr. Yupp.

12            A.   Good afternoon, Mr. Beck.

13            Q.   Mr. Yupp, could you turn please to your

14       Exhibit GJY-7?

15            A.   Okay.  I'm there.

16            Q.   What I want to do is just review the various

17       prices for fuel that were taking place in the

18       February/March time frame.

19            A.   Okay.

20            Q.   The chart at the top says "Original A3 Data."

21       Do you see that?

22            A.   Yes.

23            Q.   And that's the source of the numbers that are

24       here?

25            A.   Correct.

FLORIDA PUBLIC SERVICE COMMISSION

122

1            Q.   And just could you briefly describe what, what

2       the A3 is?

3            A.   Yes.  The A3 is basically an aggregate format,

4       all of the fuel that we used to produce our own

5       generation, in this case for the month of February.  And

6       on the A3 there's several pieces of data, but most

7       importantly total fuel cost by fuel type during the

8       month as well as the megawatt hours produced with each

9       fuel type for the month.  There's a percent mix of fuel

10       used, there's heat rate data, a lot of different data,

11       but most importantly the total fuel cost for the month.

12            Q.   And for nuclear during that time frame, you

13       have $4.44 per megawatt hour; is that right?

14            A.   That's correct.  And that would be a

15       combination of not only the Turkey Point units, but also

16       the St. Lucie units.

17            Q.   And another way to express that is about .444

18       cents per kilowatt hours.

19            A.   That is correct.

20            Q.   Is that the same thing?  And compared to that,

21       natural gas was running about .76, or 7.6 cents per

22       kilowatt hour; is that right?

23            A.   Yes.  That is correct.

24            Q.   Okay.  And so when the nuclear plants went

25       down at Turkey Point 3 and 4, customers lost the benefit

FLORIDA PUBLIC SERVICE COMMISSION

123

1       of that lower fuel price for nuclear; is that right?

2            A.   That is correct.

3            Q.   And it had to be replaced with something else.

4            A.   Correct.

5            Q.   And what you have listed in this chart here

6       are the various prices for, for other fuels that existed

7       at that time; is that right?

8            A.   That is correct.

9            Q.   And when the nuclear plants went down, you not

10       only had to run some of your own higher cost units, but

11       you also purchased power, did you not, in the open

12       market?

13            A.   We did.

14            Q.   And is that shown on GJY-9?

15            A.   Yes.  The purchased power that we procured

16       during the initial eight hours immediately following the

17       event is shown on Exhibit GJY-9.

18            Q.   And the prices that you paid ranged from about

19       12.5 cents per kilowatt hour up to 29.8 cents per

20       kilowatt hour; is that right?

21            A.   That is correct.

22            Q.   Mr. Yupp, do you have your response to the

23       staff's Interrogatory Number 42?

24            A.   I do not have a copy of it in front of me.

25            Q.   Then I will hand it to you.  And,

FLORIDA PUBLIC SERVICE COMMISSION

124

1       Commissioners, this is in staff exhibit Bate stamp 318.

2                 Staff asked you to provide a production

3       costing simulation comparing FPL's system assuming no

4       unit outages with various scenarios, did they not?

5            A.   They did.

6            Q.   And your response is contained in the response

7       to Interrogatory 42; is that right?

8            A.   That is correct.

9            Q.   And of the four -- they listed four different

10       scenarios; is that right?

11            A.   That is correct.

12            Q.   The one that simulates what actually occurred

13       is the Scenario D, is it not?

14            A.   Yes.  40 -- 42D covers the entire duration of

15       the outages that we spoke of previously today.

16            Q.   Okay.  And that's the full 158 hours for

17       Turkey Point Unit 3 being down and the full 107 hours

18       that Turkey Point Unit 4 was down; is that right?

19            A.   That is correct.

20            Q.   Could you briefly describe what it is to

21       perform, or what it is when you perform a production

22       costing simulation?

23            A.   Yes.  We used a program named GenTrader to run

24       our production cost simulation for these scenarios that

25       were laid out in this interrogatory.

FLORIDA PUBLIC SERVICE COMMISSION

125

1                 Very simply put, it is a system dispatch

2       model.  So it optimizes FPL's system based on input data

3       including generation parameter data, load forecast data,

4       fuel forecast data, and purchased power transactions,

5       sales transactions.  Whatever, whatever data we have

6       surrounding our system goes into the model.  It runs an

7       optimized system dispatch and determines a production

8       cost to meet that system dispatch.  And it can be run

9       over, from one-hour time frame to -- we run it for

10       multiple years at a time.  In this case we ran it from

11       February 26th through March 4th, which covered the

12       entire duration of the outage, and we ran it with these

13       four different scenarios.

14                 So very quickly what we ran was a base case,

15       optimized case, dispatching the system as if nothing had

16       occurred at the Flagami substation.  And then on top of

17       that we began to layer the different scenarios that

18       staff requested in this interrogatory.  42A was to run a

19       case of if Turkey Point 3 was off for 48 hours and

20       Turkey Point 4 was off for 48 hours.  So we did that.

21       We determined a production cost for that case,

22       subtracted the production cost from that case from the

23       base case, and that determines basically the replacement

24       fuel costs attributable to that specific scenario.

25                 And, likewise, we went on and did three

FLORIDA PUBLIC SERVICE COMMISSION

126

1       additional scenarios ranging from 107 hours out of

2       Turkey 4 to 158 on Turkey Point Unit 3, and then finally

3       158 on Turkey 3 and 107 on Turkey 4 as the final case

4       that we were looking at.

5            Q.   And on page -- or the attachment to your

6       response to interrogatory, let's see, assumptions you

7       used; is that correct?  The second page?

8            A.   Yes.

9            Q.   And you used the actual load that existed at

10       that time, the actual unit initial conditions and the

11       actual fuel prices that existed; is that right?

12            A.   That is correct.  We tried to replicate

13       everything we could from an actual perspective that was

14       occurring on that day.

15            Q.   Okay.  Now one difference between this and the

16       other models is that you used the ascension power which

17       occurred or a simulation of that, did you not?

18            A.   Correct.  We did with one caveat.  We, if

19       the -- in any case where we were asked to evaluate a

20       scenario in which one or the other or both Turkey Point

21       3 and 4 were off for a total of 48 hours, we did not use

22       ascension power.  We used -- to use a term that

23       Mr. Stall used, we used breaker to breaker as 48 hours.

24                 For any case in which we were asked to look at

25       158 hours for Unit 3 or 107 hours for Unit 4, we did

FLORIDA PUBLIC SERVICE COMMISSION

127

1       include the ascension power that occurred in reality as

2       those units ramp back up within that case.

3            Q.   Okay.  And your scenario for 42D, which has

4       the full outages of Unit 3 and 4, calculates the

5       replacement power costs at $14.557 million; is that

6       right?

7            A.   That is correct.

8                 MR. BECK:  Thank you, Mr. Yupp.  That's all I

9       have.

10                 COMMISSIONER SKOP:  Thank you, Mr. Beck.

11                 Ms. Bradley, the Attorney General is

12       recognized for cross-examination.

13                 MS. BRADLEY:  Thank you.

14                          CROSS EXAMINATION

15       BY MS. BRADLEY:

16            Q.   Now Turkey Point 3 was out for 158 hours;

17       correct?

18            A.   The total duration was 158 hours until it was

19       back to 100 percent power.  So the breaker closed to put

20       the unit online prior to 158, but for, for purposes of

21       getting to 100 percent power, yes, 158 hours.

22            Q.   Now the reason it took longer was because

23       y'all had to repair the rod; is that correct?

24            A.   That is my understanding.  Mr. Stall is the

25       witness that is the expert in that area of the

FLORIDA PUBLIC SERVICE COMMISSION

128

1       testimony, but that is my understanding from reading

2       testimony and listening to testimony given today.

3            Q.   Is it also your understanding that but for the

4       outage that tripped the shutdown, that you all would

5       have waited until a later date to replace the rod?

6                 MR. BUTLER:  I'm going to object to these

7       questions.  They're more appropriate for Mr. Stall.  In

8       fact, he covered those very questions earlier in his

9       testimony today.

10                 COMMISSIONER SKOP:  Ms. Helton, to the

11       objection.

12                 MS. BRADLEY:  Can I speak to the objection?

13                 COMMISSIONER SKOP:  Ms. Bradley.

14                 MS. BRADLEY:  Thank you.  He's got a lot of

15       calculations and he's making different calculations

16       apparently based upon the testimony of Mr. Stall, so I'm

17       just asking about his understanding.

18                 MS. HELTON:  Maybe Ms. Bradley could point me

19       to in the testimony of this witness where she's looking

20       and that might help me.

21                 MS. BRADLEY:  I'm looking at the same

22       interrogatory answer, Number 42, where he has different

23       calculations.

24                 MS. HELTON:  You're one ahead of me.  I don't

25       have that.  Just a second.

FLORIDA PUBLIC SERVICE COMMISSION

129

1                 MS. BRADLEY:  I'm sorry.

2                 MR. BUTLER:  Commissioner Skop, I would

3       observe in that regard if she's asking about what

4       appears on, excuse me, the answers to the interrogatory,

5       the cases that are appearing on the interrogatory were

6       defined for us by staff.  And certainly Mr. Yupp

7       addressed them, but he was not involved in proposing

8       what those cases would be that would be addressed.

9                 COMMISSIONER SKOP:  Thank you.  Ms. Bradley,

10       as a point of clarification, are you looking at the

11       calculations on Bate stamp 319 of Interrogatory Number

12       42?

13                 MS. BRADLEY:  I apologize.  I don't have a

14       Bate stamp on this copy.  I took it off of the computer.

15       But it's Interrogatory Number 42, staff's first set of

16       interrogatories.  I think it was the thing that Mr. Beck

17       was asking him about a few minutes ago.

18                 COMMISSIONER SKOP:  Thank you.  Ms. Helton, if

19       you could confer with staff to the objection.

20                 MS. HELTON:  Can I get Ms. Bradley to repeat

21       her question one more time, please?

22                 COMMISSIONER SKOP:  Ms. Bradley.

23                 MS. BRADLEY:  I will try.

24       BY MS. BRADLEY:

25            Q.   I was asking him if it was his understanding

FLORIDA PUBLIC SERVICE COMMISSION

130

1       that the reason that, that there was a difference in

2       this, at least I think this is my question, was due to

3       the fact that they had to repair the rods?

4            A.   I'm not sure if I follow a difference, and

5       what specifically are you referring to?

6            Q.   Is it your understanding that it took 158

7       hours to get the Turkey Point Unit 3 up or 100 percent,

8       I believe as you put it, was because they had to repair

9       a rod?

10                 COMMISSIONER SKOP:  Ms. Bradley, I think that

11       what I was asking was for you to restate your question

12       not to the witness but to Ms. Helton so we can rule on

13       the objection.  Sorry.

14                 MS. HELTON:  Well, it sounds like, if I'm

15       understanding the discourse that has happened here, that

16       the reason why this witness has answered this discovery

17       propounded to him was because it was laid out by staff

18       in this way.  So I'm not sure that he made the

19       connection between the reason why the different sets of

20       hours were laid out.  So it seems to me then that it

21       would be outside the scope of his cross-examination or

22       his direct testimony.

23                 COMMISSIONER SKOP:  So staff's recommendation

24       is to sustain the objection; is that correct?

25                 MS. HELTON:  Yes.

FLORIDA PUBLIC SERVICE COMMISSION

131

1                 COMMISSIONER SKOP:  Okay.  Ms. Bradley, before

2       I rule.

3                 MS. BRADLEY:  I'd like to make a proffer then

4       because I think I have the right to ask him about

5       discovery that he did and presented to staff regardless

6       of who did that.

7                 COMMISSIONER SKOP:  Let me, let me, let me

8       sustain the objection and I'll allow you to make the

9       proffer.

10                 MS. BRADLEY:  Thank you.

11       BY MS. BRADLEY:

12            Q.   Sir, is it your understanding that the reason

13       it took 158 hours to get Turkey Point 3 up to full power

14       was because they had to do a repair of a rod?

15                 MR. BUTLER:  Same objection.

16                 COMMISSIONER SKOP:  Ms. Helton.

17                 MS. HELTON:  She's proffering the witness to

18       answer the question.  So I think to lay out the record

19       for her to preserve this issue for appeal, then the

20       witness would need to answer the question.

21                 COMMISSIONER SKOP:  Yeah.

22                 THE WITNESS:  Okay.  It is my understanding

23       that a --

24                 MR. BUTLER:  I'm sorry.  Mr., Mr. Yupp, no,

25       don't answer it.  I am confused.  I thought --

FLORIDA PUBLIC SERVICE COMMISSION

132

1                 MS. BRADLEY:  Objection.

2                 MR. BUTLER:  -- there was an objection that

3       was sustained to the question.  And what Ms. Bradley is

4       doing is proffering that question into the record so

5       that it would be preserved for appeal as opposed to

6       being a live question to the witness.

7                 COMMISSIONER SKOP:  That was my understanding

8       also.  Ms. Bradley, I always --

9                 MS. BRADLEY:  I was doing a proffer to have

10       him answer so it's preserved for the record.

11                 COMMISSIONER SKOP:  The proffer would be

12       stated for the record.  I don't believe the witness

13       would respond.

14                 Ms. Helton, am I correct?

15                 MS. HELTON:  I think, Mr. Chairman, when we

16       have looked at this question in the past, there's

17       several ways to, for the proffering party to preserve

18       the record.  I believe that one of the ways and an

19       appropriate way is for Ms. Bradley to ask the question

20       and for the witness to answer the question.  And it

21       would be part of the record only for purposes of appeal

22       if she were to decide to go forward with an issue with

23       respect to that line of questioning, but it's not a part

24       of the record for the purposes of you making your

25       decision.

FLORIDA PUBLIC SERVICE COMMISSION

133

1                 COMMISSIONER SKOP:  Okay.  Very well.  The

2       objection, previous objection was sustained.

3       Ms. Bradley, I'll allow you to make the proffer.  I'll

4       allow the witness to answer the question on the advice

5       of advisory legal staff, and you may proceed.

6                 MS. BRADLEY:  I think he already has answered

7       that, and I don't know whether they're going to object

8       to the rest of my questions, but I'll proceed as though

9       we're back on the record.

10                 COMMISSIONER SKOP:  Okay.  Very well.

11       BY MS. BRADLEY:

12            Q.   Is it also your understanding that but for

13       this outage that caused the nuclear plant to trip, that

14       they would have replaced the rod or repaired the rod at

15       their next scheduled shutdown?

16                 MR. BUTLER:  I'm going to object again to this

17       as being outside the scope of Mr. Yupp's, excuse me,

18       direct testimony.

19                 COMMISSIONER SKOP:  Ms. Bradley to the

20       objection.

21                 MS. BRADLEY:  I think it goes back.  These

22       were interrogatories and part of the record, something

23       he prepared and responded to.

24                 COMMISSIONER SKOP:  Mr. Butler, with respect

25       to Mr. Stall coming back for rebuttal testimony, does he

FLORIDA PUBLIC SERVICE COMMISSION

134

1       address the, this specific issue such that Ms. Bradley

2       will have the opportunity to ask these questions on

3       rebuttal?

4                 MR. BUTLER:  It was in his direct and he did

5       address it, but we don't have an objection to his, you

6       know, clarifying that testimony in his rebuttal.

7                 COMMISSIONER SKOP:  Okay.  Very well.

8       Ms. Bradley, does that make your comfortable asking

9       Mr. Stall on his rebuttal testimony to address the

10       question subject to objection?

11                 MS. BRADLEY:  I'll be happy to save it for

12       then.  But I guess I misunderstood.  I thought he said

13       direct.

14                 MR. BUTLER:  If I -- he did address it in his

15       direct.  What I said is we would not object to having

16       you ask your questions at the time that he appears for

17       his rebuttal testimony.

18                 COMMISSIONER SKOP:  Are you comfortable with

19       that?  I think what they're, what they're -- if I

20       understand FPL correctly, is that the opportunity to ask

21       the questions would have been on the direct examination

22       of Witness Stall.  However, Witness Yupp is indicating

23       that he's not the appropriate witness to answer the

24       questions, and I think what FPL has just advised is that

25       when Witness Stall comes back for rebuttal testimony,

FLORIDA PUBLIC SERVICE COMMISSION

135

1       he'll be able to clarify and provide answers to the

2       questions you have regarding the, the replacement of the

3       control rod indicator.

4                 MS. BRADLEY:  Well, let me ask one clarifying

5       question for him.  Maybe I misunderstood.

6       BY MS. BRADLEY:

7            Q.   But did you or Mr. Stall prepare the answer to

8       staff's Interrogatory Number 42, those calculations?

9            A.   I prepared the answer to this interrogatory.

10       However, this interrogatory had already laid out the

11       scenarios, so I, I did -- the only thing I did in this

12       was take the scenarios that staff had requested in terms

13       of outage duration, whether it be 48 hours, 158 or 107,

14       depending on the unit and depending on the scenario, I

15       took those and ran the calculations.  So there was no

16       need for me to have any understanding of why Turkey

17       Point 4 was off for 107 hours, why Turkey Point 3 was

18       off for 158 hours.  I was only answering the question

19       that staff had laid out the scenario already directly

20       for me.

21            Q.   And you didn't have any information as to the

22       difference in the calculations or what they were based

23       upon?

24            A.   The calculations are based upon running a

25       production cost model with four different scenarios that

FLORIDA PUBLIC SERVICE COMMISSION

136

1       have varying levels of outage duration.  That is the

2       only information I needed to run the calculation

3       because, as I stated previously, in our production cost

4       model and as what is laid out in the answer here we took

5       actual unit conditions prior to the outage, actual load

6       forecast for the time period, actual fuel prices for the

7       time period, actual net interchange for the time period,

8       we plugged that into the model.  We ran a base case,

9       which was an optimized case giving us production costs

10       as if nothing had occurred on the system, and then we

11       slowly, one by one, case A through D, we set an outage

12       duration as requested by staff for each Turkey Point 3

13       and Turkey Point 4.  That gave us another production

14       cost answer.  Taking the difference between that in each

15       case and the base case yielded the replacement fuel cost

16       result.

17                 So, again, any detailed information as to what

18       work was done or everything that encompassed the amount

19       of time that each unit was off is not necessary to

20       answer this question.

21            Q.   So even though -- so you essentially just did

22       the number crunching and Mr. Stall would be the one that

23       could answer questions about the exhibit you prepared as

24       far as background information?

25                 MR. BUTLER:  I object to that

FLORIDA PUBLIC SERVICE COMMISSION

137

1       characterization.  I object to that characterization

2       strenuously.  The interrogatory, you know, prescribed

3       certain scenarios to which Mr. Yupp responded by doing

4       calculations per those scenarios, and it's a gross

5       distortion to be characterizing that somehow Mr. Yupp

6       didn't do his job because he didn't go behind the

7       scenarios that were prescribed to him.

8                 COMMISSIONER SKOP:  Ms. Bradley, could you

9       either respond or reframe the question in a --

10                 MS. BRADLEY:  I'm just trying to find out if

11       he can answer questions about this exhibit and the

12       differences in the numbers.  And if that's Mr. Stall,

13       then --

14                 COMMISSIONER SKOP:  Okay.  I believe -- okay.

15       Mr. Yupp, if you're able to answer that question or,

16       Ms. Bradley, if you can reframe your question, and we'll

17       see if we still have the same objection and then I'll

18       rule.

19       BY MS. BRADLEY:

20            Q.   Is it your testimony that you just crunched

21       the numbers that somebody gave you and that Mr. Stall

22       would be the person to ask about the difference in the

23       numbers and what affected that?

24            A.   No.  I can tell you why the numbers are

25       different in each scenario.  Mr. Stall would have

FLORIDA PUBLIC SERVICE COMMISSION

138

1       really -- it has nothing to do with this interrogatory.

2       This was an interrogatory that asked us to calculate

3       replacement costs based on a production cost model given

4       different scenarios of outage length.

5                 So I can tell you why the numbers are

6       different between case 42D and case 42A.  I can easily

7       explain to you why that final dollar figure is

8       different, so I am the appropriate witness for that.

9                 As far as why Turkey Point 3 was off for a

10       total of 158 hours before it reached full power, that is

11       a nuclear plant question that is, should be answered by

12       Mr. Stall, and I believe he did in his original direct

13       testimony.

14            Q.   Well, let me try a couple of more questions,

15       and if you can't answer them and want to defer to

16       Mr. Stall, then I'll let you do so.  But --

17                 COMMISSIONER SKOP:  Ms. Bradley, may I stop

18       you for one moment just to clarify something so I think

19       that we're all on the same page?

20                 Mr. Yupp, is it correct to understand that

21       basically you performed your financial analysis on the

22       replacement power costs solely based on inputs and

23       relying on those inputs provided by others in terms of

24       the scenarios?

25                 THE WITNESS:  Yes.  That is correct.

FLORIDA PUBLIC SERVICE COMMISSION

139

1                 COMMISSIONER SKOP:  Okay.  Thank you.

2                 Ms. Bradley, you may continue.

3       BY MS. BRADLEY:

4            Q.   What is the significance of the 48 hours?

5       What does that signify?

6            A.   Again, staff, staff asked us to do this

7       scenario.  So as to the significance of the 48 hours in

8       this particular interrogatory, I think that is probably

9       better addressed by staff.  But I can surmise that the

10       48-hour question was asked to us because of testimony

11       that Mr. Stall gave that that is a typical time frame

12       that a nuclear unit can be brought back after it has

13       been shut down.  And so I'm assuming that what

14       Commission staff wanted to see in that case was what

15       would the replacement power costs have been had each

16       unit returned in that 48-hour period, which is a typical

17       time frame to return a unit?

18            Q.   And the 158 hours was the time actually that

19       it took you to get it back up?

20            A.   I believe, as Mr. Stall testified to, that 158

21       hours for Unit 3 was the total duration of the time from

22       trip, from the time that the unit tripped 'til the time

23       that it reached 100 percent power.  Yes, that is

24       correct.

25            Q.   And for Turkey Point 4 it's 107 hours?

FLORIDA PUBLIC SERVICE COMMISSION

140

1            A.   That is my understanding.  Yes.

2            Q.   And do you have any understanding of why it

3       took 158 hours for Turkey Point 3 versus 107 at Turkey

4       Point 4, or is that a question for Mr. Stall?

5            A.   That is a question for Mr. Stall.

6                 MS. BRADLEY:  Okay.  I guess I will reserve

7       those questions for Mr. Stall on rebuttal.

8                 COMMISSIONER SKOP:  Very well.  Thank you,

9       Ms. Bradley.

10                 Ms. Kaufman, you're recognized for

11       cross-examination.

12                 MS. KAUFMAN:  Thank you, Commissioner.

13                          CROSS EXAMINATION

14       BY MS. KAUFMAN:

15            Q.   Mr. Yupp, if you'd turn to Page 3 of your

16       direct testimony.

17            A.   Yes.

18            Q.   And I want to ask you about your statement

19       that starts on Line 1, it goes Lines 1 through 3.

20            A.   Okay.

21            Q.   You say that, in those lines, it would be

22       unfair to FPL and serve as a major disincentive to

23       construction and operation of low fuel-cost generating

24       technologies, and I'll just paraphrase the rest, if the

25       Commission were to accept the position of Intervenors.

FLORIDA PUBLIC SERVICE COMMISSION

141

1       Is that your testimony?

2            A.   That is my testimony referencing the testimony

3       of Witness Avera.  I, that is included in my testimony

4       to set the backdrop for why the calculations were

5       performed as they were for this direct testimony.  As I

6       stated in my summary, Witness Stall and Witness Avera

7       provide in their testimony the rationale and the support

8       for the approach that FPL has taken in this.  I

9       referenced Witness Avera on this line just to set the

10       backdrop for why my calculations were done as they were

11       done.

12            Q.   So is it correct then that this isn't your

13       opinion, but you're simply relying on a statement that

14       Mr. Avera makes in his testimony?

15            A.   I am referencing -- yes.  I am referencing the

16       statements that he makes in his testimony to make it

17       clear why our calculations were done in the manner that

18       they were done.  And, yes, he, he is the witness for FPL

19       that is sponsoring that support.

20            Q.   Do you have any information to suggest that

21       FPL will operate its nuclear plants in a different

22       manner if the Commission does not accept your

23       calculations?

24            A.   No.  I have no knowledge that FPL would

25       operate any differently.  No.

FLORIDA PUBLIC SERVICE COMMISSION

142

1            Q.   And so your comments about this disincentive

2       are, are simply based on what Mr. Avera has said.

3            A.   Yes.  I am referencing Mr. Avera.

4            Q.   Sorry.  I keep mispronouncing his name.

5                 I think you've testified that you were the

6       witness in charge of doing the calculations to figure

7       out what the appropriate replacement fuel cost would be;

8       correct?

9            A.   That is correct.

10            Q.   And you presented those in your testimony

11       obviously; correct?

12            A.   Yes, I did.

13            Q.   Did you conduct any, other than the response

14       to Interrogatory Number 42 we've already discussed, did

15       you conduct any other calculations based on any other

16       methodologies for determining replacement power costs?

17            A.   Yes.  I have done numerous calculations,

18       mostly in response to interrogatories.  If I can recall

19       off the top of my head, not only 42B, which was the

20       production cost model interrogatory, but we were also

21       asked to do two additional interrogatories with four

22       cases apiece identical to 42B, one being the methodology

23       that was used in the drilled hole case.  And I believe

24       the other one was not designated how we should exactly

25       do it, so we did it twice using nuclear avoided cost and

FLORIDA PUBLIC SERVICE COMMISSION

143

1       using system average cost, again for these identical

2       four scenarios that were laid out in Interrogatory 42B.

3                 So all told, probably I've done upwards near

4       18 to 20 different calculations based on questions from

5       staff, mostly in determining what the replacement fuel

6       costs would be.

7            Q.   Prior to filing your testimony and sponsoring

8       the calculation that you suggest to the Commission, did

9       you do any other calculations or utilize any other

10       different methodologies to take a look at what

11       replacement fuel costs should be?

12            A.   Yes.  Very early, or I should say in the fall,

13       subject to check, of 2008, I responded to an

14       interrogatory on this same question as to the impact of

15       the Flagami transmission event and replacement fuel

16       costs.  Given that was the initial stages of, of, I

17       guess I'll call it, this whole proceeding to a certain

18       extent, our initial calculation through my conversations

19       with counsel were that we developed a, basically a

20       48-hour case pretty much along the lines of what Witness

21       Stall, Mr. Stall has testified to that it's pretty

22       typical that after a unit comes off the line, that it

23       could be returned to service within 48 hours.

24                 And so our initial take on this in responding

25       to that interrogatory was to run a case of 48 hours for

FLORIDA PUBLIC SERVICE COMMISSION

144

1       each unit based on nuclear avoided cost.  And that is

2       the answer that we submitted in response to

3       Interrogatory 70, I believe, subject to check, in the 08

4       docket.

5            Q.   So just so I'm clear, I think you'd agree that

6       this issue was spun out from the ongoing fuel case;

7       correct?

8            A.   That is my understanding.  Correct.

9            Q.   And in that case you provided some information

10       and calculations in which you used a 48-hour time period

11       and you used only the nuclear replacement cost; correct?

12            A.   That is correct.

13            Q.   And I guess -- would I be correct that that

14       correlates to Scenario 42A on Interrogatory Number 42?

15            A.   Yes, it does, except with one just minor

16       difference.  42A was run with a production cost model.

17       One could say that that gets a little bit more exact as

18       it's an actual model that's dispatching the system

19       economically around the different parameters it has.

20                 But, yes, you are correct, that would be an

21       identical case to the case that we supplied or the

22       answer that we supplied in Interrogatory 70.  However,

23       Interrogatory 70 was done as a manual calculation.

24            Q.   Thank you for that explanation.  And in

25       Interrogatory 70 that you provided in the fuel

FLORIDA PUBLIC SERVICE COMMISSION

145

1       adjustment case, you didn't use system average costs

2       there, you used only the nuclear power replacement

3       costs; correct?

4            A.   That is correct.

5            Q.   And the other difference I guess is that in

6       that case you used only 48 hours for the time period of

7       the outage rather than using, for example, the 158;

8       correct?

9            A.   That is correct.

10                 MS. KAUFMAN:  Okay.  Thank you, Mr. Yupp.

11       Appreciate it.

12                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

13                 Staff.

14                 MR. YOUNG:  Thank you, sir.

15                          CROSS EXAMINATION

16       BY MR. YOUNG:

17            Q.   Mr. Yupp, I have a series of questions to ask

18       you and we're going to take it one at a time because I

19       just want to, I have to fill my mind in terms of certain

20       fill in the gaps.

21                 The issue in this case revolves around how

22       much FPL should refund for the Flagami transmission

23       event that occurred on February 26th, 2008; correct?

24            A.   That is correct.

25            Q.   But for February 26th, 2008, the Flagami

FLORIDA PUBLIC SERVICE COMMISSION

146

1       transmission event, Turkey Point would not have shut

2       down for 158 hours beginning on, beginning that day;

3       correct?

4                 MR. BUTLER:  I'm going to object to the

5       question similarly to, with my objection to

6       Ms. Bradley's questions.  Mr. Yupp has made it pretty

7       clear that he's given the inputs as to the time periods

8       involved, not really the expert on the details of the

9       nuclear unit outages.

10                 COMMISSIONER SKOP:  Mr. Young, to the

11       objection.

12                 MR. YOUNG:  I can rephrase it.

13                 COMMISSIONER SKOP:  All right.

14       BY MR. YOUNG:

15            Q.   Mr. Yupp, when you were preparing your

16       testimony, did you speak to anybody as relating to the,

17       what your directions were?

18            A.   When I prepared my testimony, yes, I did.  I

19       was advised by legal counsel on the approach that FPL

20       was going to take in this case, given the circumstances

21       or the unique circumstances surrounding the event.  So,

22       yes, I did talk to counsel about FPL's approach, and

23       then subsequent to that developed a methodology that

24       would support that approach.

25            Q.   Okay.  I can move on.

FLORIDA PUBLIC SERVICE COMMISSION

147

1                 FPL's position in this docket is that the

2       Commission should require -- FPL's position in this

3       docket is that the Commission should require FPL to

4       refund the customers for eight hours for the Flagami

5       event; correct?

6            A.   That is correct.

7            Q.   And FPL wants the Commission to calculate that

8       cost using the, using what we call the system average

9       approach; correct?

10            A.   That is correct.

11            Q.   And using that system average approach, for

12       eight hours FPL calculates that it owes customers

13       $2.6 million in refunds; correct?

14            A.   That is correct.

15            Q.   But --

16            A.   I'm sorry.  I want to make sure I heard you

17       right.  $2 million you said.

18            Q.   2.6.  Is it 2 million or 2.6?

19            A.   It's 2.024 million.

20            Q.   2.024 million.

21            A.   Yes.

22            Q.   Okay.  But the actual total, but the total

23       actual cost for FPL for replacement power for the full

24       time for the Turkey Point Units 3 and 4 were, were

25       outwards of 15.9 million; correct?

FLORIDA PUBLIC SERVICE COMMISSION

148

1            A.   No.  I would say not correct.  And I

2       understand that that is, that is Witness, Dr. Dismukes'

3       calculation.  If I were going to give you an answer of

4       what the --

5            Q.   I'm sorry.  14.5.

6            A.   14 -- yes.  As described in Interrogatory 42D,

7       that would be my answer.

8            Q.   All right.  And OPC's, OPC's position and the

9       Intervenor's position is that FPL should be responsible

10       for the entire time each plant was out, and that's 158

11       hours for Turkey Point Unit 3 and 107 hours for Turkey

12       Point Unit 4; correct?

13            A.   That is my understanding of their testimony.

14       Yes.

15            Q.   And OPC's position is that the incremental

16       cost for replacement should be used; correct?

17            A.   I'm sorry.  The incremental cost for

18       replacement?

19            Q.   The cost of replacing the nuclear power plants

20       versus, instead of the system average.

21            A.   I'll answer it this way.  My understanding is

22       that OPC's argument is that as opposed to system average

23       costs being used against an incremental cost, the, they

24       propose to use a nuclear avoided cost against a system

25       incremental cost.

FLORIDA PUBLIC SERVICE COMMISSION

149

1            Q.   And that cost is 15.9 million; correct?

2            A.   That is correct.

3            Q.   So it appears that both OPC and FPL's

4       position, FPL agree or are very close to agreeing

5       mathematically that the cost of replacement due to the

6       Flagami transmission event was in between 14.5 to

7       15.9 million; correct?

8            A.   Yes.  I, I -- with one clarification.  And,

9       again, I think we talked about this, the major

10       difference being the -- while computing a manual

11       calculation, what gets left out is the ascension power

12       that occurred for that 12- to 14-hour period until the

13       units achieved 100 percent power.  And in this case it's

14       a significant amount of energy, I think totaling,

15       subject to check, about 11,600 megawatt hours between

16       both units from the time that they closed the breaker

17       until the time they reached full power.  And so that is

18       why you see -- I know we're describing it as a small

19       difference between 14.5 and 15.9, but, but it is a

20       significant difference.

21            Q.   Okay.  Now let's walk through in terms of

22       OPC's position as it relates to avoided, avoided,

23       avoided cost based on Turkey Point's 3 and 4 and the

24       system cost that FPL, FPL is advancing.

25                 Now would you agree that generation costs on a

FLORIDA PUBLIC SERVICE COMMISSION

150

1       megawatt-hour basis for Turkey Point Units 3 and 4 for

2       the months of, for the month of February was

3       approximately $4.44 per megawatt hour?

4            A.   I would agree that's a good approximation.

5       Yes.

6            Q.   And you would, and you would agree that FPL's

7       adjusted system average cost for, per megawatt hour is

8       52 -- 51.3 -- $51.32 per megawatt hour.

9            A.   Correct.  Or the adjusted system average costs

10       that I calculated, yes, 51.32 per megawatt hour.

11            Q.   And if you can turn to your Exhibit Number 7,

12       GJY-7.

13            A.   Okay.  I'm there.

14            Q.   Would you agree that you have calculated the

15       replacement generation costs based on FPL's annual

16       natural, based on FPL's natural gas and all generation,

17       all generation?

18            A.   Yes, I have.  In adjusting the system average

19       cost to reflect the time that Turkey Point Units 3 and 4

20       were off at the end of February, which is not, well,

21       which is included in the original A3 data, I felt it was

22       appropriate to go back and recalculate a system average

23       cost that would reflect both units being on in the

24       month.  And in order to do that, I did use a blended

25       cost of really the exact proportions of gas, oil and

FLORIDA PUBLIC SERVICE COMMISSION

151

1       light oil that we used during the month, which I would

2       consider to be basically FPL's marginal cost.  So

3       outside of coal, outside of nuclear, generally gas, oil

4       and light oil to a much lesser extent are on the margin

5       for FPL.

6            Q.   So the thought is that when Turkey Point,

7       Turkey Point Units 3 and 4 were offline, they were

8       replaced by natural gas, oil and light oil generation,

9       generators; correct?

10            A.   That is correct.

11            Q.   All right.  Therefore the power production

12       that cost $77.55 per megawatt hour, per megawatt hour is

13       replacing the power production costs of $4.44; correct?

14            A.   That is correct.

15            Q.   But in this case FPL is proposing that the

16       Commission assume that the $77.55 per megawatt hour is

17       replacing a power production cost of 51, $51.32 per

18       megawatt hour; correct?

19            A.   That is correct.

20            Q.   Okay.  Has the Commission ever required a

21       refund using a system average cost approach that FPL is

22       proposing?

23            A.   I, I am not aware of any time that the

24       Commission has used that to order a refund.  No.

25            Q.   But the Commission has required a refund using

FLORIDA PUBLIC SERVICE COMMISSION

152

1       the incremental cost approach proposed by OPC, correct,

2       the avoided cost approach?

3            A.   Yes.  I am aware of, of one in particular,

4       which was, I think we referred to it earlier as the

5       drilled hole case in the Turkey Point outage, extension

6       of its outage.

7            Q.   And since you mentioned drilled hole, let me,

8       let me ask you a question on the drilled hole case.  Now

9       in the drilled hole case -- and do you have a copy of

10       the drilled hole case?

11            A.   Of the order or --

12            Q.   Of the order.  Do you have an order -- a copy

13       of the order in the drilled hole case?

14            A.   I do not have it in front of me.

15                 MR. YOUNG:  May we approach, sir?

16                 COMMISSIONER SKOP:  You may.

17                 Mr. Young, you're recognized.

18                 MR. YOUNG:  Thank you, sir.

19       BY MR. YOUNG:

20            Q.   Mr. Yupp, before we get to that drilled hole

21       case, let me ask you a question.  Based on our line of

22       questioning just now, the Commission has not required a

23       system average approach to FPL's proposed, what FPL

24       proposed; correct?  It can be quick because you just

25       stated that.

FLORIDA PUBLIC SERVICE COMMISSION

153

1            A.   That they have not in the past?

2            Q.   Yes.

3            A.   Yes.  Not that I am aware of.  No.

4            Q.   But the Commission required to refund on the

5       system incremental cost approach; correct?

6            A.   In the drilled hole case, yes.

7            Q.   Okay.  Now so the Commission's decision in

8       this docket is how much of the $14.5 to $15.9 million

9       should FPL be responsible for paying and how much should

10       the ratepayers be responsible for paying; correct?

11            A.   Yes.  Well, I believe that the Commission's

12       decision in this case of how much should FPL credit back

13       to customers from the $2 million that it has filed in

14       its direct case, I'm assuming all the way up to the 15.9

15       that OPC has filed in this case.

16            Q.   And so my, so am I correct to understand that

17       FPL's argument is really a policy argument; right?

18                 MR. BUTLER:  I'm going to object to this line

19       of questions as being appropriate to Dr. Avera.  As

20       Mr. Yupp made pretty clear early on, you know, he took

21       the policy decisions, the implications of it from

22       Dr. Avera and then did the calculation.  It seems like

23       this is straying pretty far from the calculations that

24       Mr. Yupp prepared.

25                 COMMISSIONER SKOP:  Mr. Young to the

FLORIDA PUBLIC SERVICE COMMISSION

154

1       objection, specifically to Page 3 of the direct

2       testimony, Lines 1 through 6, where the witness refers

3       to FPL Witness Avera.

4                 MR. YOUNG:  Mr. Chairman, it's my

5       understanding that he, he is proposing that FPL -- he

6       is, he is aiding FPL's case that we should use a system

7       approach, a system average approach.  It's my

8       understanding that the Commission has never done that.

9       And since he's proposing those, that we use a system

10       average approach instead of an avoided cost or an

11       incremental cost approach, he, he is qualified to answer

12       the question because it relates to his testimony.

13                 Now if he, if FPL is arguing that he is not

14       the witness to, to make any statements as it relates to

15       which approach, then to me it seems like FPL's argument

16       is flawed.  Then why are they sponsoring Mr. Yupp as it

17       relates, as it relates to arguing for a system average

18       approach?

19                 MR. BUTLER:  FPL is sponsoring the testimony

20       of Mr. Yupp to perform the calculation.  Dr. Avera

21       didn't perform the calculation; Mr. Yupp did.  His role

22       is to sponsor the calculation.  It's a reasonably

23       complicated technical calculation which he prepared, and

24       he's certainly prepared to address and support how he

25       did the calculation.  But the policy questions being

FLORIDA PUBLIC SERVICE COMMISSION

155

1       asked really would be much more productively directed to

2       Dr. Avera.

3                 MR. YOUNG:  But, Mr. Chairman, if I -- and I

4       hate to belabor this point.

5                 COMMISSIONER SKOP:  Mr. --

6                 MR. YOUNG:  On Page 3 of this testimony --

7                 COMMISSIONER SKOP:  Mr. Young, briefly.

8                 MR. YOUNG:  On, on 3, on Page 3 of his

9       testimony he, he, he also, I guess he agreed with

10       Mr. Avera, said it would be unfair for FPL and serve as

11       a major disincentive in the construction and operation

12       of low fuel-generation technologies such as nuclear,

13       solar and wind if FPL were to be penalized for the

14       replacement costs using, using the avoided cost

15       approach.

16                 To me he is arguing for a system average cost

17       approach.  Thus, I can ask him if it's a policy -- since

18       the Commission has never adopted that approach --

19       whether it's a policy argument or whether it's some

20       concrete argument in terms of FPL providing some

21       documentation to show that.

22                 COMMISSIONER SKOP:  All right.  Before I go to

23       Ms. Helton, Mr. Butler, is it, are you contending FPL's

24       position is that the witness is merely performing

25       financial analysis based on inputs provided by others

FLORIDA PUBLIC SERVICE COMMISSION

156

1       and is not taking a position as to the correctness of

2       the policy that came into those inputs?

3                 MR. BUTLER:  That's a very succinct statement

4       of the position.  Thank you.

5                 COMMISSIONER SKOP:  Ms. Helton.  Ms. Helton,

6       to the objection.

7                 (Pause.)

8                 MS. HELTON:  I hear what Mr. Butler is saying

9       with respect to this witness is being offered simply to

10       perform certain calculations, and the parameters for

11       those calculations were given to him by others, either

12       by counsel or by other persons involved in putting

13       forward this case.

14                 However, I think Mr. Young does have a point.

15       When I, when I go back and I look at the line of

16       testimony that Mr. Young quoted from Page 3, it does, he

17       is expressing an opinion that it would be unfair to

18       Power & Light to serve as a major, and serve as a major

19       disinventive -- I'm sorry -- disincentive to the

20       construction and operation of low-cost generating

21       technologies such as nuclear, solar and wind if FPL were

22       to be penalized for replacement power costs associated

23       uniquely with Turkey Point Units 3 and 4 that are not a

24       result of any imprudence in the operation of those

25       units.  So it seems to me that he does have an opinion

FLORIDA PUBLIC SERVICE COMMISSION

157

1       about what type of methodology should be used to

2       determine the appropriate replacement cost.

3                 So I guess I'm a little bit confused.  Are you

4       suggesting that this particular line of testimony should

5       be struck then and he's only offering calculations or --

6       I'm having a hard time getting to why that's offered.

7                 MR. BUTLER:  No, ma'am.  What's been left out

8       of each of the quotes of that particular testimony is

9       the introductory clause for the reasons discussed by FPL

10       Witness Avera.  And immediately preceding it is another

11       statement about the nuclear outages as discussed by FPL

12       Witness Stall.  My apologies if it was not made clear

13       enough in the way we set out the testimony.

14                 But the point here is that he's simply

15       summarizing briefly what is said by FPL's other

16       witnesses, setting the stage, as he described earlier,

17       for the calculation that he performs.  He's here to

18       perform the calculation.  Mr. Stall is here to explain

19       the nuclear operations.  Dr. Avera is here to explain

20       the policy of FPL's position and will be happy to

21       address Mr. Young's questions at that time.

22                 COMMISSIONER SKOP:  Mr. Helton, does

23       Mr. Butler's response change advisory staff's opinion as

24       to the objection?

25                 MS. HELTON:  With, with that explanation, I do

FLORIDA PUBLIC SERVICE COMMISSION

158

1       think that Mr. Young's cross-examination is outside the

2       scope of the witness's testimony, and his prefiled

3       testimony should be read in that light as well.

4                 COMMISSIONER SKOP:  Okay.

5                 COMMISSIONER STEVENS:  Mr. Chairman.

6                 COMMISSIONER SKOP:  Commissioner Stevens.

7                 COMMISSIONER STEVENS:  Chairman, I'm sorry.  I

8       was trying to follow.  Mr. Butler, where does it say

9       that Mr. Yupp's testimony followed -- is based on

10       Dr. Avera's testimony?  I missed that.  I'm on Page 1 of

11       Mr. Yupp's introduction.

12                 MR. BUTLER:  No.  It's on Page 2,

13       Commissioner.  If you look at the, starting on Line

14       21 on Page 2 there are two sentences that really are

15       intending to set the stage and also specifically refer

16       to the testimony of others.  The first, "As discussed by

17       FPL witness Stall," and it goes on to talk about the

18       nuclear units remaining offline.  And then the next one

19       is "For the reasons discussed by FPL witness Avera," and

20       then goes into the policy arguments.

21                 COMMISSIONER STEVENS:  Okay.  Thank you.

22       Thank you very much.

23                 MR. BUTLER:  Certainly.

24                 COMMISSIONER SKOP:  Okay.  Based on the

25       discussion, I'm going to sustain the objection.

FLORIDA PUBLIC SERVICE COMMISSION

159

1       Mr. Young, if you would refer that question to the

2       appropriate witness when they come up for direct

3       testimony.  I believe that witness is Dr. Avera.

4                 MR. YOUNG:  Yes, sir.

5                 COMMISSIONER SKOP:  Thank you.

6       BY MR. YOUNG:

7            Q.   Well, with that said, Mr. Yupp, you have the

8       order in front of you, correct, from the drilled hole

9       incident?

10            A.   Yes, I do.

11            Q.   Let me ask you this before I start this line

12       of questioning.

13                 Are you familiar with FPL's arguments in this,

14       in this case, for the drilled hole incident?

15            A.   I am somewhat familiar at least with the

16       calculations that were done to yield the 6.1 million, I

17       believe it was, in replacement fuel costs in this case.

18       As -- I'm somewhat familiar, not, not 100 percent

19       familiar with all of the arguments, no.

20            Q.   So I guess -- let me ask you, who would be,

21       who do you believe would be more familiar with this

22       document in terms of the drilled hole incident, or maybe

23       FPL, Mr. Butler can point me to someone who can be able

24       to talk about this, this case, this order.

25                 MR. BUTLER:  Well, Dr. Avera is familiar with

FLORIDA PUBLIC SERVICE COMMISSION

160

1       the policy arguments on it.  Honestly, for the

2       calculation of the replacement power costs, if anyone

3       remembers differently, please correct me, but I believe

4       there was a stipulation of the $6.13 million figure in

5       that case.  So actually at hearing it wasn't much of a

6       topic of discussion.  The hearing was about whether or

7       not the amount was going to be disallowed.  So I don't

8       think that we have anybody that has any more familiarity

9       than Mr. Yupp does with the details of the calculation

10       that were done in that docket.

11                 MR. YOUNG:  Okay.  No further questions.

12       We'll wait for Dr. Avera.

13                 COMMISSIONER SKOP:  Thank you.

14                 Commissioners?

15                 Commissioner Stevens, you're recognized.

16                 COMMISSIONER STEVENS:  Mr. Yupp, do you know

17       how many hours customers were without power?

18                 THE WITNESS:  I do not specifically know how

19       many hours customers were without power.  No.

20                 COMMISSIONER STEVENS:  Okay.  Mr. Yupp, do you

21       know what source provided the power when the plant, two

22       plants went down?

23                 THE WITNESS:  Source from the, the replacement

24       units on our system?

25                 COMMISSIONER STEVENS:  Yes, sir.  Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

161

1                 THE WITNESS:  Or the purchase, purchases we

2       bought?

3                 COMMISSIONER STEVENS:  Both.

4                 THE WITNESS:  Both?  Units on our system, at

5       least a partial replacement was in the form of our

6       peaking units, our aircraft gas turbines, as well as

7       our, I'll call them, industrial gas turbines on the west

8       coast of Florida made up a fairly significant piece of

9       the replacement power.

10                 COMMISSIONER STEVENS:  And how are those, I'm

11       sorry, how are those turbines powered?  How does that --

12                 THE WITNESS:  The 36 aircraft gas turbines

13       that we have on the east coast of Florida are powered,

14       our dual fuel unit's primary fuel is natural gas.

15       Generally we will only run distillate or jet fuel in

16       those units if we are having a gas supply issue or

17       pressure issues.

18                 I don't recall specifically that day whether

19       we had to run jet fuel in those units.  But if we did,

20       looking at the total of jet fuel that we ran throughout

21       the month of February, it was very minimal.

22                 The other -- the additional 12 units on the

23       west coast of Florida at our Fort Myers facilities run

24       all distillate fuel oil.

25                 From a standpoint of the purchases that we

FLORIDA PUBLIC SERVICE COMMISSION

162

1       made in the market, given the, the prices that we paid

2       for that power, I would say that most of it probably

3       came from peaking units, probably upper end peaking

4       units, potentially -- I know for sure the power that we

5       bought from the DeSoto facility in DeSoto County was,

6       those are GE 7FA combustion turbines, and we bought that

7       output on distillate fuel oil.  So it was high end

8       peaking units mostly.

9                 COMMISSIONER STEVENS:  Okay.  Thank you.  And

10       one further question, if I may, Mr. Chairman.

11                 COMMISSIONER SKOP:  Go ahead.

12                 COMMISSIONER STEVENS:  Do you know where the

13       eight hours came from on the FPL calculation?

14                 THE WITNESS:  Yes.  In supporting Witness or

15       Dr. Avera in the policy issues of this and tying this to

16       the transmission event itself, and what I have written

17       in my testimony is that that eight-hour period is the

18       time period during which FPL had the most difficulty

19       operating its generating system because of all of the

20       generation that had come off the line at that one point

21       in time.

22                 And so where the calculation ended, I'll call

23       it maybe to say that the transmission event was, was

24       over and the system was back to stable was after that

25       eight-hour period when all of the gas turbines that I

FLORIDA PUBLIC SERVICE COMMISSION

163

1       just described were shut down and all of the purchased

2       power that we just talked about that we had bought in

3       response to the event had been sent back.  We were

4       starting to return and almost had returned most of the

5       gas-fired units that came off the line in response to

6       the event at that time.  And so that, that eight-hour

7       period kind of designates this is the time that the

8       transmission event had the impact on our system.  After

9       that the system was in a stable configuration again.

10                 COMMISSIONER STEVENS:  Okay.  So the system --

11       if I may, Mr. Chair.

12                 COMMISSIONER SKOP:  Continue.

13                 COMMISSIONER STEVENS:  The system was in a

14       state, it was stable, but we were using a higher cost

15       fuel.

16                 THE WITNESS:  Yes.  Again, the system was

17       stable, the, the response to the transmission event I

18       guess I'll call as in my understanding was over, and

19       I'm, I'm watching our generation screen.  So it's an

20       estimation that I'm making that once I have shut down

21       all of my peaking facilities, sent back all the

22       purchased power that I needed, that the system has now

23       become stable and that transmission event is, quote,

24       unquote, over for that period because I'm stable again.

25                 But to answer your question, yes, even after

FLORIDA PUBLIC SERVICE COMMISSION

164

1       the eight-hour period the nuclear units were off, again

2       as we have talked about for the duration.  And I think

3       we did have a couple more combustion turbines as part of

4       our gas-fired combined cycle fleet that still needed to

5       be returned, but they returned within a couple of hours.

6                 COMMISSIONER STEVENS:  Thank you, Mr. Yupp.

7       Thank you, Mr. Chair.

8                 COMMISSIONER SKOP:  Commissioners, any further

9       questions?

10                 Mr. Yupp, just two quick questions.  On Page 2

11       beginning on Line 24 and continuing on to Page 3 through

12       Line 9 of your prefiled direct testimony, again you

13       adopt the reasoning by Witness or Dr. Avera that'll be

14       coming later in this proceeding.  But you don't have a

15       specific opinion, do you, as to the appropriateness or

16       the disincentive of looking at the lower cost fuel or

17       penalizing, as the other witness will testify to?

18                 THE WITNESS:  No, I don't have an opinion on

19       that specifically, Commissioner Skop.

20                 COMMISSIONER SKOP:  Okay.  And in relation to

21       how FPL calculated its replacement fuel cost, I believe

22       on Line 7 of Page 3 it uses the eight-hour period that

23       Commissioner Stevens referred to.  I assume that was a

24       number provided to you and you just ran your analysis

25       based on that specific number; is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

165

1                 THE WITNESS:  Yes.  As far as using the

2       eight-hour period, yes.  And in understanding what FPL's

3       approach was going to be on this, that the intent was to

4       try to -- because of the uniqueness of this situation,

5       try to isolate it to the transmission event itself, I

6       felt that, as far as what I could see happen that day,

7       that in that eight-hour period was really the greatest

8       impact of the transmission event in and of itself.

9       After that the system had returned to a stable state.

10                 COMMISSIONER SKOP:  Okay.  So I'm going to ask

11       a question to you, and I'll ask in fairness the same

12       question to OPC's witness, and I'm sure I'll hear

13       differing opinions.  But am I correct to understand that

14       for that eight-hour period essentially what FPL did to

15       calculate its replacement power cost would be to take

16       the spot market price of replacement fuel and power less

17       the marginal cost of production on a systemwide basis,

18       that net cost differential being the amount that FPL

19       should refund to its customers?  Is that holistically in

20       a nutshell --

21                 THE WITNESS:  Yes.  I think in a general sense

22       that's correct.  I could just a little bit maybe

23       clarification is we took the cost of all of the peaking

24       units that I just described based on their actual fuel

25       prices for the month.  We calculated what the cost of

FLORIDA PUBLIC SERVICE COMMISSION

166

1       all of that generation was from the time they started

2       'til the time they shut down.  We added in all of the

3       purchased power that we bought on a, on a total dollar

4       basis.

5                 And I think the total was slightly over 16,600

6       megawatt hours between the peaking units we ran and the

7       purchased power we bought.  From that, as you described,

8       we subtracted the system average cost times that exact

9       same amount of megawatt hours, the net differential.

10                 COMMISSIONER SKOP:  Okay.  Like I said, I

11       could have got in deeper detail, but I was trying to say

12       it concisely.  So it's correct to understand then that

13       basically the ascension power was completely omitted

14       from that calculation.

15                 THE WITNESS:  Correct.  It would have been

16       because during that eight-hour period the units were

17       still off the line.

18                 COMMISSIONER SKOP:  Okay.  And you merely

19       performed the financial analysis based on the inputs and

20       you're taking no opinion as to the appropriateness to

21       the dollar value of the replacement fuel cost; is that

22       correct?

23                 THE WITNESS:  From the direct -- from the

24       $2 million?  Yeah.  That is correct.

25                 COMMISSIONER SKOP:  All right.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

167

1                 Okay.  Any other questions from the bench?

2                 All right.  Mr. Butler, redirect.

3                 MR. BUTLER:  Briefly.  Before I do, let me

4       note one thing.  Commissioner Stevens has asked a couple

5       of our witnesses now the question about how long

6       customers were out of, out of service, and Dr. Avera is

7       prepared to address that point when he comes to the

8       stand.  So at that time it would be appropriate to ask

9       him that question, if you choose.

10                         REDIRECT EXAMINATION

11       BY MR. BUTLER:

12            Q.   Mr. Yupp, a couple of brief redirect questions

13       for you.  You were asked by Mr. Young a question as I

14       recall it to the effect that FPL and OPC, Intervenors,

15       agree that the replacement power costs are between

16       $14.5 million and $15.9 million.  Do you remember that?

17            A.   Yes, I do.

18            Q.   Okay.  What are the conditions under which FPL

19       would agree that that is the replacement power cost

20       calculation?

21            A.   I'm not sure I follow.

22            Q.   For what scenario of outage time is that

23       appropriate?

24            A.   Both of those numbers, the 14.5 and the 15.9,

25       correlate to an outage time duration of 158 hours for

FLORIDA PUBLIC SERVICE COMMISSION

168

1       Turkey Point Unit 3 and 107 for Turkey Point Unit 4.

2            Q.   And so this would be the appropriate

3       calculation only if the Commission were to decide that

4       that's the outage duration for which it would be

5       disallowing replacement power costs; is that correct?

6            A.   That is correct.

7            Q.   Okay.  You mentioned the, one of the

8       differences between the $15.9 million calculation and

9       the $14.5 million calculation of the replacement power

10       costs for the full unit outages as being the inclusion

11       or consideration of power ascension in the system

12       simulation approach that yields the $14.5 million

13       figure.  Are there any other differences that are

14       responsible for, differences in methodology that are

15       responsible for the differences in the dollars shown in

16       those calculations?

17            A.   There probably is, and I should say there is

18       one other benefit as opposed to doing a manual

19       calculation and using a production cost model.  The

20       manual calculation is looking straightforward at a blend

21       of, in this case, gas, oil and light oil as we have

22       described.

23                 In the production cost model where the program

24       is trying to optimize system dispatch around the

25       parameters that it has, that blended cost will not

FLORIDA PUBLIC SERVICE COMMISSION

169

1       always be the case.  So, in other words, it won't be a

2       mixture of gas, oil and light oil that's always being

3       referenced against system average or nuclear avoided --

4       at night, for example, when load is lower and units

5       regulate down.  It may be looking at combined cycles

6       sitting close to their low limits as being the units

7       that, that are replacing the nuclear.  It could even be,

8       depending on how low load goes that night, it could even

9       be a little bit of coal power.

10                 So I think to a certain extent the manual

11       calculation tends to overstate because you're using a

12       static marginal value against, as I said, either system

13       average or nuclear; whereas, the production cost model

14       is really looking at how should the system have

15       dispatched what units really were on the margin?  It may

16       not be a mix; it may be gas, it may be a little coal.

17       And so that would tend to lower what the replacement

18       fuel value would be, correctly lower it.

19            Q.   Mr. Yupp, you were asked by Mr. Young whether

20       you were aware of any cases from this Commission

21       previously in which it has used the system average

22       approach that FPL proposes for calculating replacement

23       power costs, and I believe you said you were not aware

24       of any.  Are you aware of any instances where this

25       Commission has addressed the circumstance of a nuclear

FLORIDA PUBLIC SERVICE COMMISSION

170

1       unit outage having resulted from an event external to

2       the plant?

3            A.   No, I am not.  And that's partly the answer on

4       the drilled hole case and understanding the methodology

5       that was used there.  Again, a different case than what,

6       than what we face here today, and Dr. Avera will testify

7       to that.  But the circumstances surrounding this, I have

8       not, I have not seen a case such as this before.

9                 MR. BUTLER:  Thank you.  That's all the

10       redirect that I have.

11                 COMMISSIONER SKOP:  Okay.  Mr. Butler, I just

12       want to speak briefly before we get to the exhibits.

13       Again, Mr. Yupp came real close to opening a door there.

14       I just want to clarify that I sustained the previous FPL

15       objection on the basis that Dr. Avera would be the

16       appropriate witness to answer staff's line of questions,

17       and it was not intended to impede staff's ability to get

18       the answers to its questions.  So, again, let staff ask

19       those questions when they have the appropriate witness

20       onboard.  But if we don't get the answers, then again I

21       think staff still reserves the right to ask these

22       questions again even if they're not, the witnesses

23       aren't able to answer them.  But, again, I just want to

24       make the parties clear as to the objection was sustained

25       based on the representations that he was not the

FLORIDA PUBLIC SERVICE COMMISSION

171

1       appropriate witness.

2                 MR. BUTLER:  Understood.  And that's, that,

3       that is certainly fair.  And if by some chance their

4       questions lead to something about calculation, we

5       certainly wouldn't object to Mr. Yupp being asked those

6       questions when he comes back for rebuttal.

7                 COMMISSIONER SKOP:  Okay.  Well, like I say,

8       just in the rebuttal he gave, came real close to

9       offering an opinion as to policy.  So I didn't want to

10       have that door opened if he's not the appropriate

11       witness.

12                 With respect to -- if that concludes your

13       redirect, I guess we need to address exhibits.

14                 MR. BUTLER:  Thank you.  Yes.  We would move

15       the admission of Exhibits 2 through 10.

16                 COMMISSIONER SKOP:  Okay.  Any objection from

17       the parties?  Okay.  I'm showing no objection.  Exhibits

18       2 through 10 will be entered into the record.

19                 (Exhibits 2 through 10 admitted into the

20       record.)

21                 And, staff, any additional matters before we

22       call the next witness?

23                 MS. BENNETT:  No, sir.

24                 COMMISSIONER SKOP:  Okay.  Mr. Butler, if you

25       could call your next witness.

FLORIDA PUBLIC SERVICE COMMISSION

172

1                 MR. BUTLER:  We would call Dr. Avera.

2                 (Pause.)

3                 COMMISSIONER SKOP:  And to our court reporter,

4       Linda, are you doing all right or do you need to take a

5       break any time soon?  Okay.  Thank you.

6                 Mr. Butler, you're recognized.

7                 MR. BUTLER:  Thank you.  Dr. Avera has been

8       previously sworn.

9                           WILLIAM E. AVERA

10       was called as a witness on behalf of Florida Power &

11       Light Company and, having been duly sworn, testified as

12       follows:

13                          DIRECT EXAMINATION

14       BY MR. BUTLER:

15            Q.   And I would ask that he state his name and

16       business address for the record.

17            A.   William E. Avera, 3907 Red River, Austin,

18       Texas.

19            Q.   By whom are you employed and in what capacity?

20            A.   I am the President of FINCAP, Incorporated, an

21       economic and financial consulting firm.

22            Q.   Have you prepared and caused to be filed in

23       this proceeding 13 pages of prefiled direct testimony on

24       January 13, 2010?

25            A.   Yes.

FLORIDA PUBLIC SERVICE COMMISSION

173

1            Q.   Do you have any changes or corrections to make

2       to your prefiled direct testimony?

3            A.   No, I do not.

4            Q.   Okay.  If I asked you the questions contained

5       in your prefiled direct testimony today, would your

6       answers be the same?

7            A.   Yes.

8                 MR. BUTLER:  Okay.  Commissioner Skop, I'd ask

9       that Dr. Avera's prefiled direct testimony be inserted

10       into the record as though read.

11                 COMMISSIONER SKOP:  The prefiled testimony of

12       the witness will be entered into the record as though

13       read.

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

187

1                 MR. BUTLER:  And Dr. Avera's testimony, direct

2       testimony does not have any exhibits, so at this point I

3       would ask him to summarize his testimony.

4                 THE WITNESS:  Good afternoon, Commissioners.

5       My testimony examines the proper regulatory treatment of

6       the replacement power costs from the February 26th,

7       2008, transmission event.  Basing the cost of

8       replacement fuel exclusively on the Turkey Point nuclear

9       units would be unfair and would undermine incentives for

10       energy-efficient technologies.  The replacement cost

11       calculation presented by Mr. Yupp recognizes that this

12       outage was triggered by a transmission event and not

13       plant imprudence.  It is fair to FPL's customers and

14       avoids disincentives for utilities to invest in

15       energy-efficient and environmentally beneficial

16       generation alternatives.

17                 As described in the testimony of FPL witness

18       Stall, the transmission event caused the Turkey Point

19       units to automatically trip offline as they were

20       designed to do.  Turkey Point's costs should not be used

21       exclusively in calculating the replacement cost because

22       100 percent of the benefits of nuclear fuel cost are

23       passed on to FPL's customers.  If this low nuclear fuel

24       cost is used to penalize FPL for an outage that was not

25       caused by nuclear operations, a clear message will be

FLORIDA PUBLIC SERVICE COMMISSION

188

1       sent to investors and FPL and other Florida electric

2       utilities that investing in low fuel cost alternatives

3       has become a more risky, asymmetrical proposition.  The

4       larger the cost difference from the system average, the

5       greater the penalty from a disallowance unrelated to

6       plant operations.

7                 Investors understand when they invest in a low

8       fuel cost alternative that they are exposed to the risk

9       of high replacement cost when plant operations are

10       imprudent.  But what is new and what is not built into

11       investor expectations is that they would be exposed to

12       high replacement costs from an outage that is unrelated

13       to plant operations.  That increases the risk and it

14       would undermine the state's policy of encouraging

15       energy-efficient, environmentally beneficial and

16       economically necessary investment.  That completes my

17       summary.

18                 MR. BUTLER:  Thank you, Dr. Avera.  I tender

19       the witness for cross-examination.

20                 COMMISSIONER SKOP:  Very well.  Thank you,

21       Mr. Butler.

22                 Mr. McGlothlin, you're recognized for

23       cross-examination.

24                 MR. McGLOTHLIN:  Thank you, Commissioner.

25                          CROSS EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

189

1       BY MR. McGLOTHLIN:

2            Q.   Hello, Dr. Avera.  I'm Joe McGlothlin with

3       OPC.

4            A.   Hello, Mr. McGlothlin.  Good to see you again.

5            Q.   Thank you, sir.  I first want to refer you to

6       Page 7 of your direct testimony.

7            A.   Yes, sir.

8            Q.   Since the last time you and I had a

9       conversation on the record, I've traded my old lenses in

10       for some new ones, and so I have to bounce back and

11       forth between my spectacles and you.  The difference is

12       I can see you without the spectacles now.  That was not

13       possible before.  But please pardon as I, as I deal with

14       that little situation.

15                 But I want to refer you to Page 7, Line 4

16       through 11, and the statement by you that, "Under

17       Florida's fuel and power adjustment clauses, a utility

18       has an opportunity to recover its actual fuel costs.

19       The best outcome for the utility is that the dollars it

20       has paid are fully recovered from customers, with no

21       opportunity for gain.  On the other hand, if some of the

22       utility's expenditures are deemed to have been

23       imprudent, then those costs are not recovered from

24       customers.  Thus, utility investors see an asymmetric

25       risk exposure in clause recovery, with no upside

FLORIDA PUBLIC SERVICE COMMISSION

190

1       opportunity and a potentially large downside."  My

2       question refers to the statement about an asymmetric

3       risk exposure in clause recovery.

4                 Now on the prior page, Page 6, you refer to a

5       fundamental tenet of what you would characterize as a

6       regulatory compact is that the utility is entitled to an

7       opportunity to recover from customers all reasonable and

8       necessary costs prudently incurred in providing service,

9       do you not?

10            A.   Yes.

11            Q.   And would you agree with me that the recovery

12       of fuel costs through a clause is a subpart of that

13       larger picture fundamental tenet?

14            A.   That is correct.  That the -- unless there has

15       been a finding of prudence, imprudence by the

16       Commission, the utility ought to be able to recover that

17       cost.

18            Q.   And would you agree that it also follows that

19       if a utility has incurred unreasonable costs, it is not

20       entitled to recover those from customers?

21            A.   That is correct.  And as happens with some

22       frequency, the utility does not recover those costs and,

23       therefore, its return, its profit suffers.

24            Q.   And translating that fundamental tenet that

25       you describe on Page 6 to what I would be, characterize

FLORIDA PUBLIC SERVICE COMMISSION

191

1       as the counterpart mathematical equation that we see in,

2       for instance, revenue requirement cases, you are

3       familiar, are you not, with the equation that says the

4       total revenues a utility is going to collect is a

5       function of its reasonably incurred expenses plus a fair

6       return on prudently invested capital?

7            A.   That is correct.  That's a good summary.

8            Q.   Referring to the rate case scenario by

9       analogy, isn't it true that with respect to what we

10       characterize as operations and maintenance costs, O&M,

11       the best that the utility can do is to recover what it

12       incurred and there's some downside in the event the

13       Commission deems a portion of those costs as imprudent

14       or unreasonable?

15            A.   Well, as a technical matter, Mr. McGlothlin,

16       that's not correct.  Because generally for at least

17       fixed O&M costs they are established at the time of the

18       rate case.  And if those O&M costs go down because of

19       economic conditions or because of management efficiency,

20       it is possible for management to actually benefit

21       because its actual O&M costs are different than those

22       that are built into the base rates.

23                 So as to those O&M costs that are impounded in

24       the base rates, there is not a dollar-for-dollar

25       recovery as occurs for fuel costs and those variable O&M

FLORIDA PUBLIC SERVICE COMMISSION

192

1       costs that might be recovered through a clause.

2            Q.   That variance though is a function not of any

3       action by the Commission to mark up O&M, but is instead

4       a function of the different frequency with which base

5       rates are adjusted to track actual costs; isn't that

6       correct?

7            A.   Well, it's a function of many things,

8       Mr. McGlothlin.  It's a function of what happens to

9       those costs relative to what is built into base rates.

10       Those costs could go down because of economic

11       circumstances beyond the control of management or they

12       could go up because of those same reasons.  They could

13       also go down because management has found new

14       efficiencies, better and cheaper ways of doing things.

15       So there are any number of reasons why the O&M expenses

16       that are actually incurred can vary from those that are

17       built into base rates.

18            Q.   Yes.  I agree with your characterization which

19       says that over time the actual experience can depart

20       either above or below what was assumed or incorporated

21       in the, in the calculation of revenues.

22                 But focusing for a moment on the ratemaking

23       exercise itself and using the example, for instance, of

24       wages, labor rates that, that are not capitalized as

25       part of construction, just straightforward labor rates,

FLORIDA PUBLIC SERVICE COMMISSION

193

1       at the time those are quantified in the revenue

2       requirements case, there's no markup or profit added to

3       those costs, are there?

4            A.   That is correct.  And the Commission reviews

5       those and it may find them, some are imprudently high

6       and it adjusts them down and builds into the base rates

7       the number, the prudent -- that the Commission believes

8       is representative of reasonable and prudent management

9       going forward.

10                 But the profit that the utility gets is built

11       into the fair rate of return on rate base.  But it's

12       important to understand that whenever there's a

13       disallowance of an expense that the company actually

14       incurred like a fuel expense, then the effect is to

15       lower the rate of return.

16                 As Mr. Beck, I think, might have incorrectly

17       stated, if, if there are expenses that aren't recovered,

18       it does affect the rate of return of the company.

19            Q.   And that is because the company and not the

20       ratepayers are absorbing those costs that have been

21       deemed unreasonable by the Commission; correct?

22            A.   That is correct.  Those that have been paid

23       but aren't ultimately recovered from customers, then

24       management pays those out of shareholder funds, so to

25       speak.

FLORIDA PUBLIC SERVICE COMMISSION

194

1            Q.   Then you agree with me that focusing on the

2       ratemaking exercise specifically in the context of the

3       revenue requirements case, the manner in which the

4       Commission treats wages, copier paper, the gasoline that

5       is burned in the utility's trucks does not differ from

6       the way that fuel costs are covered in that those are

7       quantified as precisely as the base rate mechanism

8       allows without profit, and the best that the utility can

9       do is recover what it actually incurs, and there is the

10       corresponding downside as, as there is with the fuel in

11       the event the regulator determines that any of those was

12       imprudent?

13            A.   Mr. McGlothlin, I can't agree with you for the

14       reasons we've discussed.  The base rates are set.  The

15       company collects the base rates.  Whatever its expenses

16       are are what they are.  And to the extent that those

17       deviate from what is built in base rates, the company

18       comes out ahead or behind.  This is very different in my

19       mind from the fuel part of the collections where there

20       is a reconciliation of what the company actually paid.

21       So if fuel prices have gone down since the fuel factor

22       was set, then the reconciliation will return money to

23       the customers, just as if they've gone up, it will

24       collect extra money for the customers.  So there is a

25       dollar-for-dollar reconciliation.

FLORIDA PUBLIC SERVICE COMMISSION

195

1                 The only exception as I understand it, now

2       there's like the GPIF and a few other things to the

3       side, but in the main the company either gets to collect

4       its fuel cost or it doesn't if they're found to be

5       imprudent.  It can't get extra dollars to contribute to

6       its profit from those fuel expenditures.

7            Q.   You did agree with me that at the time the

8       Commission sets base rates, those O&M costs are

9       quantified with as much precision as possible to be

10       reflective of what the utility is going to incur;

11       correct?

12            A.   That's right.

13            Q.   Okay.  That's my --

14            A.   But once the base rates are set, the world

15       spins.

16            Q.   One step at a time, Dr. Avera, please.

17            A.   Yes, sir.

18            Q.   You also agree that at that point in time

19       during the ratemaking exercise no profit is added to O&M

20       such as wages, gasoline, copier paper; correct?

21            A.   That is correct.

22            Q.   And you agreed with me that at the time those

23       base rates are set, the Commission does review those

24       expenses to determine whether any should be disallowed

25       by virtue of being unreasonable in amount; correct?

FLORIDA PUBLIC SERVICE COMMISSION

196

1            A.   Unreasonable or unnecessary or any number of

2       other reasons, yes.

3            Q.   So with respect to those aspects of the base

4       rate exercise and those aspects of the fuel cost

5       recovery exercise, those are treated in a similar

6       manner, are they not?

7            A.   That is correct as to the initial setting.

8       It's what happens later that makes the difference.

9            Q.   Now you referred to the aspect of Florida's

10       fuel cost recovery clause that enables the utility to

11       recover dollar for dollar, and that is by virtue of the

12       true-up mechanism, is it not?

13            A.   Yes, sir.

14            Q.   Because absent the true-up mechanism, as is

15       the case with base rates, the actual experience may very

16       well depart from what is incorporated in the fuel cost

17       recovery factor per se.

18            A.   It may, and often does sometimes dramatically,

19       because fuel prices are volatile.

20            Q.   But under Florida's fuel cost recovery clause,

21       the utility has the opportunity to demonstrate that it

22       has collected either more or less than was projected and

23       the difference is added to the, or subtracted from that

24       amount with interest taken into account; correct?

25            A.   That is correct.  So that the best that can

FLORIDA PUBLIC SERVICE COMMISSION

197

1       happen is it recover what it actually spent ultimately

2       after the reconciliation and the subsequent periods

3       except to those specific items that had been disallowed.

4            Q.   Would you agree with me then that with respect

5       to fuel cost recovery in Florida, from the investor's

6       standpoint, the investor sees less downside risk with

7       respect to fuel than it does in the base rate mechanism

8       because there's no true-up mechanism there?

9            A.   No, I can't agree.  I think it depends on what

10       the investor believes about the ability of management to

11       manage its O&M costs and the other costs that are in

12       base rates relative to its exposure on the fuel side to

13       disallowances.  So -- and the fuel is, is much bigger

14       than O&M.  It, it's a huge part of the cost of service.

15       So it's a very big pot, so that a small difference can

16       make a big difference to investors.

17            Q.   But you do acknowledge that with respect to

18       the base rate mechanism, that ratemaking exercise does

19       not incorporate a true-up aspect.

20            A.   It does not.

21            Q.   Now you alluded to the fact that with respect

22       to the utility's opportunity to make a profit or return,

23       that is associated with the part of the equation that

24       says revenue requirements shall include a fair return on

25       prudently invested capital; correct?

FLORIDA PUBLIC SERVICE COMMISSION

198

1            A.   That's correct.  That is the profit that's

2       built in the base rates.  The actual profit that the

3       utility earns depends on how the world turns out, how

4       its expenses relate to what is in base rates and whether

5       or not it's able to collect all of its fuel expenses,

6       and of course its investment and capital costs change

7       over time.

8            Q.   Let's focus on the -- that half of the

9       equation.  Take the hypothetical example of a utility

10       that spends $8 billion to build a new nuclear unit and

11       then approaches the Commission to place that in rate

12       base, and assume that the Commission determines that it

13       should have cost only $7 billion.  In that scenario what

14       amount of the investment would be placed in the

15       company's rate base?  What would it return?

16            A.   Well, the Commission would put into rate base

17       that investment that they regard to have been prudently

18       incurred.  So irrespective of what the company actually

19       spent, what is put in rate base, and I think in your

20       hypothetical it was $6 million, what was the number,

21       billion?

22            Q.   The investment was eight and the Commission

23       determines that seven was --

24            A.   If the Commission determines that 7 billion is

25       the prudent amount, that's what goes in the rate base

FLORIDA PUBLIC SERVICE COMMISSION

199

1       and that's what the company is allowed to earn on.

2            Q.   So even with respect to the profits half of

3       that equation from the investor's standpoint there is

4       the potential of what you referred to as a downside, and

5       that is the possibility that the company, the company

6       may not see the entire investment placed in rate base

7       where it's going to earn a return.

8            A.   That is correct.  That is one of the risks

9       that goes with being a utility, that you have to invest

10       as wisely and carefully as possible because this

11       Commission has the ability to review what you've done.

12       And if this Commission finds that you have not spent all

13       of those dollars prudently, then the customers will not

14       be responsible for them.

15            Q.   So also in that regard there is a parallel to

16       be drawn between the base rate function on the one hand

17       and fuel cost recovery in that in both instances the

18       Commission performs a screening function to protect

19       customers from unreasonable amounts, and in both

20       situations the best that the company and its investors

21       can, can do is to see 100 percent of the amount spent

22       reflected in rates.

23            A.   That's the best they can do.  Now their actual

24       earnings of course depend on how events turn out.  But

25       this Commission's role in the world, and it's a hard

FLORIDA PUBLIC SERVICE COMMISSION

200

1       world -- a hard role but an extremely important one, is

2       to review the expenditures that utilities make and make

3       sure that they are reasonable and prudently incurred.

4       And then for those expenditures and for those

5       investments, set rates that gives the company a

6       reasonable opportunity to earn a fair rate of return.

7            Q.   With respect to your testimony on the fuel

8       cost issue in this case, you have referred to that as an

9       asymmetrical risk exposure, do you not?

10            A.   Yes.

11            Q.   Let's take another simple hypothetical, and

12       the hypothetical is that the utility has expended

13       $100,000 on fuel costs and the Commission has determined

14       that $10,000 of that $100,000 was imprudently incurred

15       and unreasonable in amount and allows the utility to

16       pass through to the customers only $90,000.  And so that

17       would keep it as simple as possible.  Let's say there's

18       no, there's no issue about the finding of imprudence.

19       That's not contested, it's certain, and the disallowance

20       is made.  Would you agree that in that situation the

21       investors cannot expect the customers to collect, to pay

22       the entire $100,000?

23            A.   No.  If, if an expenditure is found imprudent,

24       then the effect is that the company can only collect the

25       $90,000.  Its investors absorb the ten, the customers

FLORIDA PUBLIC SERVICE COMMISSION

201

1       only pay the 90.

2                 Now it's really important that the Commission

3       consider the consequences of its prudent decision

4       because it will affect the behavior of the utility and

5       others.  So it needs to make sure that in finding this

6       imprudence it has properly considered the facts and has

7       not created any perverse incentives that have unintended

8       consequences that end up hurting the customers.

9                 COMMISSIONER SKOP:  Mr. McGlothlin, do you

10       have -- how much longer of cross-examination do you

11       have?  This may be a good breaking point otherwise.

12                 MR. McGLOTHLIN:  Possibly another 30 minutes

13       or so.

14                 COMMISSIONER SKOP:  Okay.  If you wouldn't

15       mind, it looks like we're about ready to switch out

16       court reporters, so I'd like to take a brief break and

17       we'll come back at 3:15.

18                 (Recess taken.)

19                 (Transcript continues in sequence with Volume

20       2.)

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

202

1       STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2       COUNTY OF LEON      )

3

4                 I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing

5       proceeding was heard at the time and place herein

stated.

6

IT IS FURTHER CERTIFIED that I

7       stenographically reported the said proceedings; that the

same has been transcribed under my direct supervision;

8       and that this transcript constitutes a true

transcription of my notes of said proceedings.

9

I FURTHER CERTIFY that I am not a relative,

10       employee, attorney or counsel of any of the parties, nor

am I a relative or employee of any of the parties'

11       attorneys or counsel connected with the action, nor am I

financially interested in the action.

12

DATED THIS _____ day of _____________________,

13       2010.

14

15                  ________________________________

LINDA BOLES, RPR, CRR

16                 FPSC Official Commission Reporter

(850) 413-6734

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION