## Notes
Asbestos Disposal Costs (Waste Management - Pensacola)
$55.00/ton
$45.00/drum
$150.00/load (minimum)
$175.00/load (Direct Burial Fee)
Asbestos Insulation density is 12 pounds per cubic foot (dry) per Bill Gusnard (Mechanical design.
Bill says that equipment/pipe insulation at the bouiler house averages 6" thick and 4" thick elsewhere.
Assume average thickness for all to be 5' (for calculations).
Perdido and Pea Rea Ridge contain no Asbestos.
Daniel contains no Asbestos.
Scherer Asbestos is handled by separate ARO and is not included in the Studies.

## Plant Scholz
Facility Name: | Plant Scholz |  |  |  |  | FINAL - 10-12-05
Year Online:
| Number of Buildings: | 9 |  |  |  |  | Number of Buildings with suspect ACMs: | 7
SUMMARY
Building # | Building Name |  | Quantity |  |  | Potential ARO
|  |  | linear ft | ft2 | ft3 |  |  | NOTE: The boilers are included with the generators and are listed as Buildings 2 and 3.
1 | Main Plant |  | 0 | 135576 | 0 | 613642
2 | Generating Unit and Boiler 1 |  | 0 | 33197 | 0 | 456298 | [7 empty] | 227819 | SF
3 | Generating Unit and Boiler 2 |  | 0 | 36641 | 0 | 476306 | [7 empty] | 94924.5833 | CF @ 5" Thick
4 | Baghouse Control Room |  | 0 | 1800 | 0 | 14400 | [7 empty] | 12 | lb/cf density
5 | Warehouse - No ACMs |  | 0 | 0 | 0 | 0 | [7 empty] | 1139095 | Pounds
6 | Quonset Hut #1 |  | 0 | 11520 | 0 | 23040 | [7 empty] | 569.5475 | Tons | 55 | 31325.1125 | Dump Fees
7 | Quonset Hut 2 |  | 0 | 7085 | 0 | 17095
8 | Old Fire Pump House (outside the fence) |  | 0 | 2000 | 0 | 8000 | [7 empty] | 3515.7253 | CY
9 | Fire Pump House - No ACMs |  | 0 | 0 | 0 | 0 | [7 empty] | 439.4657 | Loads at 8cy/load | 175 | 76906.4911 | Direct Burial Fees
[5 empty] | FACILITY-WIDE ESTIMATED ARO | 1608781 |  | 227819 | 7.0617
[6 empty] | (Removal & Disposal Costs) | [10 empty] | 108231.6036 | Disposal Costs
Suspect Asbestos Containing Materials - Building 1:
Building: | Main Plant
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Abatement Cost per Unit | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y |  |  |  |  | 77012 |  | 4 | 308048 |  | 4
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y |  |  |  |  | 25150 |  | 3 | 75450 |  | 3
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | Preciptiators |  |  |  | 15000 |  | 12 | 180000 |  | 12
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic |  |  |  | Y |  |  |  |  | 4536 |  | 3 | 13608 |  | 3
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation |  |  |  | Y |  |  |  |  | 878 |  | 12 | 10536 |  | 12
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal |  |  |  | Y |  |  |  |  | 13000 |  | 2 | 26000 |  | 2
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 135576 | 0 |  | 613642
Suspect Asbestos Containing Materials - Building 2
Building: | Generating Unit and Boiler 1
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y |  |  |  |  | 14596 |  | 16 | 233536 |  | 16
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y |  |  |  |  | 9000 |  | 12 | 108000 |  | 12
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y |  |  |  |  | 6975 |  | 14 | 97650 |  | 14
TI | Tank Insulation |  |  |  | Y |  |  |  |  | 226 |  | 12 | 2712 |  | 12
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y |  |  |  |  | 2400 |  | 6 | 14400 |  | 6
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 33197 | 0 |  | 456298
Suspect Asbestos Containing Materials - Building 3
Building: | Generating Unit and Boiler 2
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y |  |  |  |  | 14666 |  | 16 | 234656 |  | 16
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y |  |  |  |  | 9000 |  | 12 | 108000 |  | 12
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y |  |  |  |  | 6975 |  | 14 | 97650 |  | 14
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y |  |  |  |  | 6000 |  | 6 | 36000 |  | 6
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 36641 | 0 |  | 476306
Suspect Asbestos Containing Materials - Building 4
Building: | Baghouse Control Room
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings |  |  |  | Y |  |  |  |  | 1800 |  | 8 | 14400 |  | 8
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 1800 | 0 |  | 14400
Suspect Asbestos Containing Materials - Building 5:
Building: | Warehouse - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 6
Building: | Quonset Hut #1
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal |  |  |  | Y |  |  |  |  | 11520 |  | 2 | 23040 |  | 2
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 11520 | 0 |  | 23040
Suspect Asbestos Containing Materials - Building 7
Building: | Quonset Hut 2
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile |  |  |  | Y |  |  |  |  | 2925 |  | 3 | 8775 |  | 3
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal |  |  |  | Y |  |  |  |  | 4160 |  | 2 | 8320 |  | 2
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 7085 | 0 |  | 17095
Suspect Asbestos Containing Materials - Building 8
Building: | Old Fire Pump House (outside the fence)
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y |  |  |  |  | 2000 |  | 4 | 8000 |  | 4
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 2000 | 0 |  | 8000
Suspect Asbestos Containing Materials - Building 9
Building: | Fire Pump House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0

## Plant Smith
Facility Name: | Plant Smith |  |  |  |  | FINAL 10-12-05
Year Online:
| Number of Buildings: | 16 |  |  |  |  | Number of Buildings with suspect ACMs: | 8
SUMMARY
Building # | Building Name |  | Quantity |  |  | Potential ARO
|  |  | linear ft | ft2 | ft3 |  |  | NOTE: The boilers are included with the generators and are listed as Buildings 11 and 12 in the summary spreadsheet. | [8 empty] | Density of Asbestos Gaskets: 109 lb/cf
1 | Office |  | 0 | 5760 | 0 | 23040 | [10 empty] | http://www.equalseal.com/product-p/tfe-env-d7590-na-0600-18-150.htm
2 | Safety Supply House - No ACMs |  | 0 | 0 | 0 | 0 | [5 empty] | 252182 | SF
3 | Tank Storage House |  | 0 | 480 | 0 | 1440 | [5 empty] | 105075.8333 | CF @ 5" Thick |  |  |  | Assume typical size of pipe in a Fire Pump House to be 6". Gasket would be 2" wide X 3/16" thick X 22" long.
4 | Tank Farm - No ACMs |  | 0 | 36900 | 0 | 147600 | [5 empty] | 12 | lb/cf density
5 | Plant Offices |  | 0 | 8800 | 0 | 35200 | [5 empty] | 1260910 | Pounds |  |  |  | 7" x pi is 22" long.
6 | Oil House - No ACMs |  | 0 | 0 | 0 | 0 | [5 empty] | 630.455 | Tons | 55 | 34675.025 | Dump Fees
7 | Coal Conveyor House - No ACMs |  | 0 | 0 | 0 | 0 | [10 empty] | 2" x 3/16"x 22" = |  | 8.25 | cubic inches
8 | Precipitators - No ACMs |  | 0 | 0 | 0 | 0 | [5 empty] | 3891.6975 | CY
9 | Demineralizer House - No ACMs |  | 0 | 0 | 0 | 0 | [5 empty] | 486.4622 | Loads at 8cy/load | 175 | 85130.8835 | Direct Burial Fees | 1 | gasket | 0.0047743 | cubic feet
10 | Main Plant - Excluding Generators & Boiler Units |  | 0 | 63424 | 0 | 190892
11 | Boiler & Generator No. 1 |  | 0 | 84194 | 0 | 1158458 | [8 empty] | 119805.9085 | Disposal Costs | 1 | gasket | 0.5204 | pounds/ea
12 | Boiler & Generator No. 2 |  | 0 | 49624 | 0 | 658718
13 | Tan Building - No ACMs |  | 0 | 0 | 0 | 0 | [10 empty] | 400 | gaskets | 208.1597 | pounds (total)
14 | Fire Pump House |  | 400 | 2000 | 0 | 8000
15 | Warehouse |  | 0 | 1000 | 0 | 3000
16 | Building w/ Flag - No ACMs |  | 0 | 0 | 0 | 0
[5 empty] | FACILITY-WIDE ESTIMATED ARO | 2226348 |  | 252182 |  |  |  | 8.8283
(Removal & Disposal Costs)
Suspect Asbestos Containing Materials - Building 1:
Building: | Office
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Abatement Cost per Unit | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum |  |  |  | Y |  |  |  |  | 5760 |  | 4 | 23040
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 5760 | 0 |  | 23040
Suspect Asbestos Containing Materials - Building 2
Building: | Safety Supply House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 3
Building: | Tank Storage House
Building Size:
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y |  |  |  |  | 480 |  | 3 | 1440
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 480 | 0 |  | 1440
Suspect Asbestos Containing Materials - Building 4
Building: | Tank Farm - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [8 empty] | 36900 |  | 4 | 147600
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 36900 | 0 |  | 147600
Suspect Asbestos Containing Materials - Building 5:
Building: | Plant Offices
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | Cable Spreading Room |  |  |  | 3800 |  | 4 | 15200
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum |  |  |  | Y |  |  |  |  | 5000 |  | 4 | 20000
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 8800 | 0 |  | 35200
Suspect Asbestos Containing Materials - Building 6
Building: | Oil House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 7
Building: | Coal Conveyor House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 8
Building: | Precipitators - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 9
Building: | Demineralizer House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 10
Building: | Main Plant - Excluding Generators & Boiler Units
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y |  |  |  |  | 63300 |  | 3 | 189900
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings |  |  |  | Y |  |  |  |  | 124 |  | 8 | 992
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 63424 | 0 |  | 190892
Suspect Asbestos Containing Materials - Building 11
Building: | Boiler & Generator No. 1
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y |  |  |  |  | 39855 |  | 16 | 637680
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y |  |  |  |  | 32193 |  | 12 | 386316
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y |  |  |  |  | 6355 |  | 14 | 88970
TI | Tank Insulation |  |  |  | Y |  |  |  |  | 1791 |  | 12 | 21492
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y |  |  |  |  | 4000 |  | 6 | 24000
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 84194 | 0 |  | 1158458
Suspect Asbestos Containing Materials - Building 12
Building: | Boiler & Generator No. 2
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y |  |  |  |  | 18630 |  | 16 | 298080
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y |  |  |  |  | 20639 |  | 12 | 247668
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y |  |  |  |  | 6355 |  | 14 | 88970
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y |  |  |  |  | 4000 |  | 6 | 24000
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 49624 | 0 |  | 658718
Suspect Asbestos Containing Materials - Building 13
Building: | Tan Building - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 14
Building: | Fire Pump House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y |  |  |  |  | 2000 |  | 3 | 6000
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: Gaskets |  |  |  |  | RANDY AYERS |  |  | 400 |  |  | 5 | 2000
[8 empty] | FACILITY TOTALS: | 400 | 2000 | 0 |  | 8000
Suspect Asbestos Containing Materials - Building 15
Building: | Warehouse
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic |  |  |  | Y |  |  |  |  | 1000 |  | 3 | 3000
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 1000 | 0 |  | 3000
Suspect Asbestos Containing Materials - Building 16
Building: | Building w/ Flag - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[9 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [10 empty] | 4 | 0
BI | Boiler Insulation | [10 empty] | 16 | 0
BUR | Built Up Roof | [10 empty] | 3 | 0
CT | Ceiling Tile | [10 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [10 empty] | 12 | 0
FP | Fire Proofing | [10 empty] | 16 | 0
FCL | Floor Covering Linoleum | [10 empty] | 4 | 0
FTM | Floor Tile & Mastic | [10 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [10 empty] | 14 | 0
TI | Tank Insulation | [10 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [10 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [10 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [10 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [10 empty] | 6 | 0
OTR | Other: | [11 empty] | 0
[8 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0

## Plant Crist
Facility Name: | Plant Crist |  |  |  |  | FINAL 10-12-05
Year Online:
| Number of Buildings: | 42 |  |  |  |  | Number of Buildings with suspect ACMs: |  | 34
SUMMARY
Building # | Building Name |  | Quantity |  |  | Potential ARO
|  |  | linear ft | ft2 | ft3 |  |  | NOTE: The boilers are included with the generators and are listed as Buildings 34 to 38, 40, and 41 in the summary spreadsheet.
1 | Main Plant - Excluding Generator Unit & Boilers |  | 0 | 175024 | 0 | 700896
2 | Cooling Tower Nos. 1-5 |  | 0 | 28480 | 0 | 113920
3 | Cooling Tower No. 6 - No ACMs |  | 0 | 0 | 0 | 0
4 | Cooling Tower No. 7 |  | 0 | 36900 | 0 | 147600
5 | Cooling Tower Pump House - No ACMs |  | 0 | 0 | 0 | 0
6 | Breaker Building - Units 1-5 |  | 0 | 875 | 0 | 2625
7 | Hydrogen Building - No ACMs |  | 0 | 0 | 0 | 0
8 | Battery House |  | 0 | 300 | 0 | 900
9 | Annex Building - Offices |  | 0 | 19616 | 0 | 72664
10 | Fire House - No ACM |  | 0 | 0 | 0 | 0
11 | Breaker Building - No ACMs |  | 0 | 0 | 0 | 0
12 | Coal Dock Offices |  | 0 | 4448 | 0 | 13344
13 | Tractor Garage |  | 0 | 1895 | 0 | 9780
14 | Tractor Shed - No ACMs |  | 0 | 0 | 0 | 0
15 | Coal Hopper House |  | 0 | 7800 | 0 | 31200
16 | Fuel Handling Electrical Shop |  | 0 | 2804 | 0 | 11216
17 | Process Conveyor Hood |  | 0 | 2804 | 0 | 11216
18 | Feed Conveyor Hood |  | 0 | 5850 | 0 | 23400
19 | Crusher House |  | 0 | 5760 | 0 | 23040
20 | Feed Conveyor |  | 0 | 7380 | 0 | 29520
21 | Conveyor Overflow House |  | 0 | 400 | 0 | 2100
22 | Fire Pump House (Units 3, 4, &5) |  | 0 | 1324 | 0 | 8636
23 | Tank No. 1 - Fire Water |  | 0 | 232 | 0 | 3248 | [6 empty] | 591298 | SF
24 | Water Intake Pump House Shed |  | 0 | 3850 | 0 | 15400 | [6 empty] | 246374.1667 | CF @ 5" Thick
25 | Warehouse |  | 0 | 72800 | 0 | 225600 | [6 empty] | 12 | lb/cf density
26 | Feed Conveyor (Units 6 & 7) |  | 0 | 12600 | 0 | 50400 | [6 empty] | 2956490 | Pounds
27 | Feed House #1 |  | 0 | 1800 | 0 | 7200 | [6 empty] | 1478.245 | Tons | 55 | 81303.475 | Dump Fees
28 | Chlorine Shed |  | 0 | 1260 | 0 | 5040
29 | Waste Oil House |  | 0 | 3960 | 0 | 15840 | [6 empty] | 9124.9691 | CY
30 | #3 Water Treatment Plant |  | 0 | 308 | 0 | 924 | [6 empty] | 1140.6211 | Loads at 8cy/load | 175 | 199608.6998 | Direct Burial Fees
31 | #2 Water Treatment Plant - No ACMs |  | 0 | 100 | 0 | 300
32 | Plant Diesel Fire Pump #7 |  | 0 | 100 | 0 | 300 | [9 empty] | 280912.1748 | Disposal Costs
33 | Cooling Water Lab - No ACMs |  | 0 | 0 | 0 | 0
34 | Generator Unit & Boiler 3 |  | 0 | 12768 | 0 | 184288
35 | Generator Unit & Boiler 2 |  | 0 | 14606 | 0 | 190920
36 | Generator Unit & Boiler 1 |  | 0 | 14652 | 0 | 191472
37 | Generator Unit & Boiler 4 |  | 0 | 33406 | 0 | 500800
38 | Generator Unit & Boiler 5 |  | 0 | 43409 | 0 | 602832
39 | Coal Feed Roof - Unit 6 |  | 0 | 4860 | 0 | 14580
40 | Generator Unit & Boiler 6 |  | 0 | 16920 | 0 | 155854
41 | Generator Unit & Boiler 7 |  | 0 | 43151 | 0 | 597262
42 | Unit 7 Coal Feed Roof |  | 0 | 8856 | 0 | 26568
[5 empty] | FACILITY-WIDE ESTIMATED ARO | 3990885 |  | 591298 | 6.7494 |  |  |  | 3990906.7212
(Removal & Disposal Costs)
Suspect Asbestos Containing Materials - Building 1:
Building: | Main Plant - Excluding Generator Unit & Boilers
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Abatement Cost per Unit | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 174924 |  | 4 | 699696
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 100 |  | 12 | 1200
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 175024 | 0 |  | 700896
Suspect Asbestos Containing Materials - Building 2
Building: | Cooling Tower Nos. 1-5
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | Louvers |  |  |  |  | 28480 |  | 4 | 113920
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 28480 | 0 |  | 113920
Suspect Asbestos Containing Materials - Building 3
Building: | Cooling Tower No. 6 - No ACMs
Building Size:
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 4
Building: | Cooling Tower No. 7
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [9 empty] | 36900 |  | 4 | 147600
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 36900 | 0 |  | 147600
Suspect Asbestos Containing Materials - Building 5:
Building: | Cooling Tower Pump House - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 6
Building: | Breaker Building - Units 1-5
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 875 |  | 3 | 2625
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 875 | 0 |  | 2625
Suspect Asbestos Containing Materials - Building 7
Building: | Hydrogen Building - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 8
Building: | Battery House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 300 |  | 3 | 900
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 300 | 0 |  | 900
Suspect Asbestos Containing Materials - Building 9
Building: | Annex Building - Offices
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic |  |  |  | Y | [5 empty] | 15360 |  | 3 | 46080
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 1256 |  | 14 | 17584
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) |  |  |  | Y | [5 empty] | 3000 |  | 3 | 9000
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 19616 | 0 |  | 72664
Suspect Asbestos Containing Materials - Building 10
Building: | Fire House - No ACM
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 11
Building: | Breaker Building - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 12
Building: | Coal Dock Offices
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile |  |  |  | Y | [5 empty] | 1848 |  | 3 | 5544
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) |  |  |  | Y | [5 empty] | 2600 |  | 3 | 7800
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 4448 | 0 |  | 13344
Suspect Asbestos Containing Materials - Building 13
Building: | Tractor Garage
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile |  |  |  | Y | [5 empty] | 1580 |  | 3 | 4740
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing |  |  |  | Y | [5 empty] | 315 |  | 16 | 5040
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 1895 | 0 |  | 9780
Suspect Asbestos Containing Materials - Building 14
Building: | Tractor Shed - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [11 empty] | 5 | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 15
Building: | Coal Hopper House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 7800 |  | 4 | 31200
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 7800 | 0 |  | 31200
Suspect Asbestos Containing Materials - Building 16
Building: | Fuel Handling Electrical Shop
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | Interior & Exterior |  |  |  |  | 2804 |  | 4 | 11216
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 2804 | 0 |  | 11216
Suspect Asbestos Containing Materials - Building 17
Building: | Process Conveyor Hood
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 13500 |  | 4 | 54000
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 13500 | 0 |  | 54000
Suspect Asbestos Containing Materials - Building 18
Building: | Feed Conveyor Hood
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [9 empty] | 5850 |  | 4 | 23400
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 5850 | 0 |  | 23400
Suspect Asbestos Containing Materials - Building 19
Building: | Crusher House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [9 empty] | 5760 |  | 4 | 23040
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 5760 | 0 |  | 23040
Suspect Asbestos Containing Materials - Building 20
Building: | Feed Conveyor
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 7380 |  | 4 | 29520
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 7380 | 0 |  | 29520
Suspect Asbestos Containing Materials - Building 21
Building: | Conveyor Overflow House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 300 |  | 3 | 900
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 100 |  | 12 | 1200
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 400 | 0 |  | 2100
Suspect Asbestos Containing Materials - Building 22
Building: | Fire Pump House (Units 3, 4, &5)
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 900 |  | 3 | 2700
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 424 |  | 14 | 5936
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 1324 | 0 |  | 8636
Suspect Asbestos Containing Materials - Building 23
Building: | Tank No. 1 - Fire Water
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 232 |  | 14 | 3248
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 232 | 0 |  | 3248
Suspect Asbestos Containing Materials - Building 24
Building: | Water Intake Pump House Shed
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 3850 |  | 4 | 15400
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 3850 | 0 |  | 15400
Suspect Asbestos Containing Materials - Building 25
Building: | Warehouse
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 72000 |  | 3 | 216000
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 800 |  | 12 | 9600
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 72800 | 0 |  | 225600
Suspect Asbestos Containing Materials - Building 26
Building: | Feed Conveyor (Units 6 & 7)
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 12600 |  | 4 | 50400
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 12600 | 0 |  | 50400
Suspect Asbestos Containing Materials - Building 27
Building: | Feed House #1
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 1800 |  | 4 | 7200
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 1800 | 0 |  | 7200
Suspect Asbestos Containing Materials - Building 28
Building: | Chlorine Shed
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 1260 |  | 4 | 5040
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 1260 | 0 |  | 5040
Suspect Asbestos Containing Materials - Building 29
Building: | Waste Oil House
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels |  |  |  | Y | [5 empty] | 3960 |  | 4 | 15840
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 3960 | 0 |  | 15840
Suspect Asbestos Containing Materials - Building 30
Building: | #3 Water Treatment Plant
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile |  |  |  | Y | [5 empty] | 308 |  | 3 | 924
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 308 | 0 |  | 924
Suspect Asbestos Containing Materials - Building 31
Building: | #2 Water Treatment Plant - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 32
Building: | Plant Diesel Fire Pump #7
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 100 |  | 3 | 300
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 100 | 0 |  | 300
Suspect Asbestos Containing Materials - Building 33
Building: | Cooling Water Lab - No ACMs
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 0 | 0 |  | 0
Suspect Asbestos Containing Materials - Building 34
Building: | Generator Unit & Boiler 3
Building Size:
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 10768 |  | 16 | 172288
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 2000 |  | 6 | 12000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 12768 | 0 |  | 184288
Suspect Asbestos Containing Materials - Building 35
Building: | Generator Unit & Boiler 2
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 6912 |  | 16 | 110592
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 5694 |  | 12 | 68328
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 2000 |  | 6 | 12000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 14606 | 0 |  | 190920
Suspect Asbestos Containing Materials - Building 36
Building: | Generator Unit & Boiler 1
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 6912 |  | 16 | 110592
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 5740 |  | 12 | 68880
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 2000 |  | 6 | 12000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 14652 | 0 |  | 191472
Suspect Asbestos Containing Materials - Building 37
Building: | Generator Unit & Boiler 4
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 21060 |  | 16 | 336960
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 2400 |  | 12 | 28800
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 9044 |  | 14 | 126616
TI | Tank Insulation |  |  |  | Y | [5 empty] | 502 |  | 12 | 6024
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 400 |  | 6 | 2400
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 33406 | 0 |  | 500800
Suspect Asbestos Containing Materials - Building 38
Building: | Generator Unit & Boiler 5
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 21060 |  | 16 | 336960
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside |  |  |  | Y | [5 empty] | 2400 |  | 12 | 28800
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 10842 |  | 14 | 151788
TI | Tank Insulation |  |  |  | Y | [5 empty] | 5107 |  | 12 | 61284
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 4000 |  | 6 | 24000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 43409 | 0 |  | 602832
Suspect Asbestos Containing Materials - Building 39
Building: | Coal Feed Roof - Unit 6
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 4860 |  | 3 | 14580
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 4860 | 0 |  | 14580
Suspect Asbestos Containing Materials - Building 40
Building: | Generator Unit & Boiler 6
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 3840 |  | 3 | 11520
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 5687 |  | 14 | 79618
TI | Tank Insulation |  |  |  | Y | [5 empty] | 3393 |  | 12 | 40716
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 4000 |  | 6 | 24000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 16920 | 0 |  | 155854
Suspect Asbestos Containing Materials - Building 41
Building: | Generator Unit & Boiler 7
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation |  |  |  | Y | [5 empty] | 22584 |  | 16 | 361344
BUR | Built Up Roof | [11 empty] | 3 | 0
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation |  |  |  | Y | [5 empty] | 12557 |  | 14 | 175798
TI | Tank Insulation |  |  |  | Y | [5 empty] | 2010 |  | 12 | 24120
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic |  |  |  | Y | [5 empty] | 6000 |  | 6 | 36000
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 43151 | 0 |  | 597262
Suspect Asbestos Containing Materials - Building 42
Building: | Unit 7 Coal Feed Roof
Observed Potential ACMs
Material |  |  |  |  | Observed? Y/N | Location(s) |  |  |  | Quantity |  |  | Potential Liablility | MATERIAL TOTAL
[10 empty] | linear ft | ft2 | ft3 | $
ACP | Asbestos Cement (Transite) Panels | [11 empty] | 4 | 0
BI | Boiler Insulation | [11 empty] | 16 | 0
BUR | Built Up Roof |  |  |  | Y | [5 empty] | 8856 |  | 3 | 26568
CT | Ceiling Tile | [11 empty] | 3 | 0
IDI | Duct Insulation-Exterior/Outside | [11 empty] | 12 | 0
FP | Fire Proofing | [11 empty] | 16 | 0
FCL | Floor Covering Linoleum | [11 empty] | 4 | 0
FTM | Floor Tile & Mastic | [11 empty] | 3 | 0
PI | Pipe Insulation - Thermal Systems Insulation | [11 empty] | 14 | 0
TI | Tank Insulation | [11 empty] | 12 | 0
WB | Wall Board (Sheet Rock) | [11 empty] | 3 | 0
OTR | Other: Exterior Textured Coatings | [11 empty] | 8 | 0
OTR | Other: Silver Coating on Metal | [11 empty] | 2 | 0
OTR | Other: Turbine Cover Mastic | [11 empty] | 6 | 0
OTR | Other: | [12 empty] | 0
[9 empty] | FACILITY TOTALS: | 0 | 8856 | 0 |  | 26568