## Reporting_FEECA_Com_clean
Measure Name | EndUse | Algorithm 1 | Algorithm 2 | Parameter | Attribute | Units | Source
Efficient Exhaust Hood | Cooking | delta_kWh = kWhbase-kWheff |  | ExHood_kWhbase | 18980 | kWh | PG&E Workpaper: Energy Management Systems (EMS) and Demand-controlled Kitchen Ventilation (DCKV) Energy Savings in Restaurants 2014
Efficient Exhaust Hood | Cooking | delta_kWh = kWhbase-kWheff |  | ExHood_kWheff | 10913.5 | kWh | PG&E Workpaper: Energy Management Systems (EMS) and Demand-controlled Kitchen Ventilation (DCKV) Energy Savings in Restaurants 2014
Energy Star Combination Oven | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | ComOven_Days | 365 | days | 2018 Current Energy Star https://www.energystar.gov/products/commercial_food_service_equipment provided caluclator "commercial_kitchen_equipment_calculator_0"
Energy Star Combination Oven | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | ComOven_ENERGYeff | 32.6411 | kWh/day | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Combination Oven | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | ComOven_ENERGYbase | 50.0877 | kWh/day | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Fryer | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) |  | ESFryer_kWhEff | 4273.6313 | kWh/Year | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx for Large Vat Fryer
Energy Star Fryer | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) |  | ESFryer_kWhBase | 5177.4536 | kWh/Year | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx for Large Vat Fryer
Energy Star Griddle | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | ESGriddle_ENERGYbase | 43.3288 | kWh/day | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Griddle | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Days | 365 | Days/Year
Energy Star Griddle | Cooking | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | ESGriddle_ENERGYeff | 38.0959 | kWh/day | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Hot Food Holding Cabinet | Cooking | delta_kWh= (PIDLE,BASE - PIDLE,EFF) / 1000 x HOU |  | ESFoodCab_HOU | 5475 | Hours | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Hot Food Holding Cabinet | Cooking | delta_kWh= (PIDLE,BASE - PIDLE,EFF) / 1000 x HOU |  | ESFoodCab_PIDLEbase | 600 | W | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Hot Food Holding Cabinet | Cooking | delta_kWh= (PIDLE,BASE - PIDLE,EFF) / 1000 x HOU |  | ESFoodCab_PIDLEeff | 284 | W | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Steamer | Cooking | delta_kWh = ESSteam_kWhbase - ESSteam_kWheff |  | ESSteam_kWheff | 5387.9111 | kWh/Year | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Energy Star Steamer | Cooking | delta_kWh = ESSteam_kWhbase - ESSteam_kWheff |  | ESSteam_kWhbase | 15123.4535 | kWh/Year | 2018 Current Energy Star https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator_0.xlsx
Induction Cooktops | Cooking | delta_kWh= (IndCook_kWbase - IndCook_kWee-IndCook_HVAC_cooling) / 1000 x HOU |  | IndCook_Hours | 2056.5 | Hours | Minnesota TRM version 2.2, Commercial Food Service - Electric Oven and Range
Induction Cooktops | Cooking | delta_kWh= (IndCook_kWbase - IndCook_kWee-IndCook_HVAC_cooling) / 1000 x HOU |  | IndCook_kWee | 4140 | W | Minnesota TRM version 2.2, Commercial Food Service - Electric Oven and Range
Induction Cooktops | Cooking | delta_kWh= (IndCook_kWbase - IndCook_kWee-IndCook_HVAC_cooling) / 1000 x HOU |  | IndCook_HVAC_cooling | 1.03 |  | Minnesota TRM version 2.2, Commercial Food Service - Electric Oven and Range
Induction Cooktops | Cooking | delta_kWh= (IndCook_kWbase - IndCook_kWee-IndCook_HVAC_cooling) / 1000 x HOU |  | IndCook_kWbase | 5100 | W | Minnesota TRM version 2.2, Commercial Food Service - Electric Oven and Range
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Electric Resistance Water Heater Existing Efficiency, 50 Gallon (EFBASE) | 0.904 |  | Federal Standard 2004-2014 (based on 50 gallon)
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Temperature of Hot Water Heater (THOT) | 125 | °F | Illinois TRM, Version 5.0,Volume 3: Residential Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 5.4.2, page 167
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Electric Resistance Water Heater Baseline Efficiency, 50 Gallon (EFBASE) | 0.945 | % | Code
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Assumed temperature of water entering house (Tcold) in FL Zone 1 (FPL) | 79.24 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-North | 74.15 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-Central | 77.43 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Drain Water Heat Recovery Energy Savings Factor (SVGE) | 0.12273 | % | Minnesota 2016 Statewide TRM V1.3, Residential Hot Water - Drainpipe Heat Exchanger with Electric Water Heater (adjusted for Florida groundwater temp)
Drain Water Heat Recovery | Domestic Hot Water | delta_kWh = [HW x 8.33 x (THOT - TCOLD) / EFBASE] / 3412 x SVGE |  | Annual Gallons of Hot Water Use (HW) | See Table Below | Gal | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-69
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | BldgEnergy_Base_Zone 2 | 16700.9612 | kWh | Calculated from the above parameters
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | BoosterEnergy_Base | 13137.4326 | kWh | Calculated from individual parameters below
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | IdleEnergy_Base | 4234 | kWh | Calculated from individual parameters below
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | BldgEnergy_Efficient | 9063.8101 | kWh | Calculated from the above parameters
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | BoosterEnergy_Efficient | 9063.8101 | kWh | Calculated from the above parameters
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | IdleEnergy_Efficient | 3406.6667 | kWh | Calculated from individual parameters below
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Number of racks washed per day (RW) | 280 |  | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | BTU per kWh | 3412 | BTU/kWh
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Typical wash time (Twash) | 1 | min | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Efficiency of water heater (EFFHt) | 0.98 |  | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Density of Water (wdensity) | 8.33 | lbs/gal | Wisconsin FoTechnical Reference Manual
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Average daily hours of dishwasher operation (Hours) | 18 | hours | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Idle power draw (kW) of baseline dishwasher (IdleDrawBase) | 0.87 | kW | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Annual days of dishwasher operation (D) | 365 | days | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Water use per rack (gal) of ENERGY STAR dishwasher (WaterUseESTAR) | 0.89 | gal | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Water use per rack (gal) of baseline dishwasher (WUB) | 1.29 | gal | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Inlet water temperature increase (Tin)_bldg Zone 1 | 45.76 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Inlet water temperature increase (Tin)_bldg Zone 2 North | 50.85 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Inlet water temperature increase (Tin)_bldg Zone 2 Central | 47.57 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Inlet water temperature increase (Tin)_booster | 40 | deg F | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Energy Star Commercial Dishwasher | Domestic Hot Water | delta_kWh = (BldgEnergy_base + BoosterEnergy_base + IdleEnergy_base)-(BldgEnergy_eff + BoosterEnergy_eff + IdleEnergy_eff) | BldgEnergy,BoosterEnergy=[(WUB*RW*D)*(Tin*Twash*8.33/EffHt/3412)]-[(WaterUseESTAR*RW*D)*(Tin*Twash*8.33/EffHt/3,412)] IdleEnergy = [IdleDrawBase*(Hours*D – D*RW*Twash/60)] –[IdleDrawESTAR*(Hours*D – D*RW*Twash/60)] | Idle power draw (kW) of ENERGY STAR dishwasher (IdleDrawESTAR) | 0.7 | kW | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.2.6, page 41 & 42
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Average flow rate of the low-flow faucet aerator (GPMlow) | 1 | gpm | Measure Definition
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Average flow rate in gallons per minute of the baseline faucet (GPMbase) | 1.39 | gpm | DeOreo, B., and P. Mayer. Residential End Uses of Water Study Update. Forthcoming. ©2015 Water Research Foundation. Reprinted With Permission
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Estimated usage of mixed water per faucet (Usage) | 5000 | gallons/year | Illinois TRM, Version 5.0,Volume 2: Commercial and Industrial Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 4.3.2, page 95
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Energy per gallon of water used by faucet (elec WH) (GPGelectric) | 0.040957 | Calculated from the parameter listed below
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Assumed temperature of mixed water (WaterTemp) | 91 | deg F | Cadmus and Opinion Dynamics Showerhead and Faucet Aerator Meter Study Memorandum dated June 2013, directed to Michigan Evaluation Working Group.
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Assumed temperature of water entering house (Tcold) in FL Zone 1 (FPL) | 79.24 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Assumed temperature of water entering house (Tcold) in FL Zone 2-North | 74.15 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Assumed temperature of water entering house (Tcold) in FL Zone 2-Central | 77.43 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Recovery efficiency of electric water heater (Re_electric) | 0.98 |  | Electric water heaters have recovery efficiency of 98%: http://www.ahridirectory.org/ahridirectory/pages/home.aspx.
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Conversion from kWh to BTU (kWhBTU) | 3412 | BTU/kWh
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Specific Weight of Water (WaterWeight) | 8.33 | lb/gal
Faucet Aerator | Domestic Hot Water | delta_kWh = ((GPMbase - GPMlow)/GPMbase) x Usage x EPGelectric | EPGelectric = (8.33 * 1.0 * (WaterTemp - SupplyTemp))/(RE_electric * 3412) | Heat capacity of water (HeatCapWater) | 1 | BTU/lb-deg F
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Efficient Heat Pump Water Heater Energy Factor (EFEFF) | 2 |  | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-71
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Electric Resistance Water Heater Baseline Efficiency, 50 Gallon (EFBASE) | 0.945 | % | Code
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | HP Water Heater water temperature delta between inlet and outlet (TDELTA) in FL Zone 1 | 48 | °F | Average Groundwater temperature of Florida https://www3.epa.gov/ceampubl/learn2model/part-two/onsite/ex/jne_henrys_map.html. Assumed water heater setpoint is 125 F
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Annual Gallons of Hot Water Use (HW) | See Table Below | Gal | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-69
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | HP Water Heater Resistive Discount Factor (RDF) | 0.9 |  | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-71
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Heat Pump Water Heater COP Adjustment Factor (FADJUST) | 1.09 |  | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-71
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | HP Water Heater water temperature delta between inlet and outlet (TDELTA) in FL Zone 1 (FPL) | 45.76 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | HP Water Heater water temperature delta between inlet and outlet (TDELTA) in FL Zone 2-North | 50.85 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | HP Water Heater water temperature delta between inlet and outlet (TDELTA) in FL Zone 2-Central | 47.57 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls. Assumed water heater setpoint is 125 F
Heat Pump Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Electric Resistance Water Heater Existing Efficiency, 50 Gallon (EFBASE) | 0.904 |  | Federal Standard 2004-2014 (based on 50 gallon)
Hot Water Circulation Pump Control | Domestic Hot Water | kWh = (Wattsbase/1000*HOURSbase)-(Wattsee/1000*HOURSee) |  | Demand Controlled Circulating Systems Deemed Energy Savings (delta_kWh) | 651 | kWh/pump | Illinois 2015 Statewide Technical Reference Manual, Section 4.3.8
Hot Water Circulation Pump Control | Domestic Hot Water | kWh = (Wattsbase/1000*HOURSbase)-(Wattsee/1000*HOURSee) |  | Domestic Hot Water Energy Use Intensity (EUIDomestic Hot Water) | See Table Below | kWh/ft2/yr | Gulf LoadMap Commercial Results
Hot Water Circulation Pump Control | Domestic Hot Water | kWh = (Wattsbase/1000*HOURSbase)-(Wattsee/1000*HOURSee) |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Circumference of piping | 0.196 | ft | Assumes 3/4" diameter pipe.
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Temperature difference between water in pipe and ambient air (T) | 55 | deg F | Assumes 125 F water leaving the hot water tank and average temperature of conditioned space of 70 F
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | DHW Recovery efficiency (RE_DHW) | 0.98 |  | Electric water heaters have recovery efficiency of 98%.
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Assumed R-value of existing uninsulated piping (Rexit) | 1 | hr-deg F-ft/Btu | Navigant Consulting Inc., April 2009; “Measures and Assumptions for Demand Side Management (DSM) Planning; Appendix C Substantiation Sheets”, p77.
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Assumed length of piping insulated for commercial sector (L) | 60 | ft | Engineering Assumption
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Conversion factor (BTU_conv) | 3412 | BTU/kWh
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | Hours per year | 8760 | hours
Hot Water Pipe Insulation | Domestic Hot Water | delta_kWh = ((1/Rexist – 1/Rnew) * (L * C) * T * Hours)/ RE_DHW / BTU_conv |  | R-value of existing pipe plus installed insulation (Rnew) | 5 | hr-deg F-ft/Btu | Estimated value based on recommendation of Illinois TRM. Supported by minimum set by 2012 IECC = R-3. U.S. Department of Energy, August 2012.
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Instantaneous Hot Water System Energy Factor Rating for Efficient equipment (EFEFF) | 0.98 | 0 | Electric Tankless Water Heating: Competitive Assessment, EPRI Retail Technology Application Centers, March 2005.
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Temperature of Instantaneous Hot Water System Tank (TOUT) | 119 | °F | Engineering Assumption
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Instantaneous Hot Water System Energy Factor Rating for Baseline equipment (EFBASE) | 0.9227 | 0 | Federal minimum uniform energy factor for a 40 gallon electric storage water heater with a medium draw pattern = 0.9307-(.0002*40)
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Density of Water (wdensity) | 8.33 | lbs/gal | Wisconsin FoTechnical Reference Manual
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Annual Gallons of Hot Water Use (HW) | See Table Below | Gal | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-69
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 1 (FPL) | 79.24 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-North | 74.15 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Instantaneous Hot Water System | Domestic Hot Water | delta_kWh = (1/ EFbase - 1/EFefficient) * (HW* y_Water * (TOUT – Tin) * 1.0 )/3,412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-Central | 77.43 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Shower Water Temperature (TSHOWER) | 105 | °F | Minnesota 2016 Statewide TRM V1.3
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Average Number of Showers per Showerhead per Day (SPERSON/DAY) | 0.5 | Showers/Day/Showerhead | Deemed
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Baseline Showerhead Flow Rate (GPMBASE) | 2.5 | GPM | Federal Standard Minimum Showerhead Flow Rate
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Existing Showerhead Flow Rate (GPMBASE) | 2.7778 | GPM | Assumed 10% less efficient than baseline
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Assumed temperature of water entering house (Tcold) in FL Zone 1 (FPL) | 79.24 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-North | 74.15 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-Central | 77.43 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Average Per Person Gallons of Shower Water Use per Day (GPERSON/DAY) | 17.2 | Gallons/Person/Day | Minnesota 2016 Statewide TRM V1.3
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Efficient Showerhead Flow Rate (GPMEFF) | 1.75 | GPM | Measure Definition
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Showerhead Measures Energy to Demand Factor (ETDF) | 0.000813 | kW/kWh | Pennsylvania 2016 Statewide TRM, Section 2.3.9, Table 2-67
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Recovery Efficiency of Water Heater (RE) | 0.98 |  | Pennsylvania 2016 Statewide TRM, Section 2.3.8, Table 2-66
Low Flow Shower Head | Domestic Hot Water | delta_kWh = (GPMBASE - GPMEFF) x GPERSON/DAY x NOSHOWER x SPERSON/DAY x 365 x (TSHOWER - TCOLD) x 8.33) / 3412 x RE |  | Average Number of Showerheads (NOSHOWER) | See Table Below
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Baseline Sprayer Flow Rate (GPMBASE) | 2.25 | GPM | Pennsylvania 2016 Statewide TRM, Section 3.4.2, Table 3-74
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Efficient Sprayer Flow Rate (GPMEFF) | 1.12 | GPM | Pennsylvania 2016 Statewide TRM, Section 3.4.2, Table 3-74
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Efficient Sprayer Water Usage (TIMEBASE) | 2190 | Minutes | Pennsylvania 2016 Statewide TRM, Section 3.4.2, Table 3-74
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Baseline Sprayer Water Usage (TIMEBASE) | 1752 | Minutes | Pennsylvania 2016 Statewide TRM, Section 3.4.2, Table 3-74
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Existing Sprayer Flow Rate (GPMBASE) | 2.475 | GPM | Assumed 10% less efficient than code
Low-Flow Pre-Rinse Sprayers | Domestic Hot Water | delta_kWh = [(GPMBASE x TIMEBASE) - (GPMEFF x TIMEEFF)] x .1333 |  | Sprayers Energy to Demand Factor (ETDF) | 0.000178 | kW/kWh | Pennsylvania 2016 Statewide TRM, Section 3.4.2, Table 3-74
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Electric Resistance Water Heater Baseline Efficiency, 50 Gallon (EFBASE) | 0.945 | % | Code
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Annual Gallons of Hot Water Use (HW) | See Table Below | Gal | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-69
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Temperature of Hot Water Heater (THOT) | 125 | °F | Illinois TRM, Version 5.0,Volume 3: Residential Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 5.4.2, page 167
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Efficient Solar Water Heater Energy Factor (EFEFF) | 4.05 |  | The average rating for all evaluated water heaters across the 3 zones in Florida (FSEC)
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Electric Resistance Water Heater COP Adjustment Factor (FADJUST) | 1 |  | Pennsylvania 2016 Statewide TRM, Section 3.4.1, Table 3-71
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 1 (FPL) | 79.24 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-North | 74.15 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Assumed temperature of water entering house (Tcold) in FL Zone 2-Central | 77.43 | °F | FSEC Solar Water Heater Calculator, http://www.fsec.ucf.edu/en/consumer/solar_hot_water/homes/calculator/SHW-calculator_simple.xls
Solar Water Heater | Domestic Hot Water | delta_kWh = {[1/EFBASE - (1/EFEFF x 1/FADJUST)] x HW x 8.33 x 1.0 x (Thot - Tcold)} / 3412 |  | Electric Resistance Water Heater Existing Efficiency, 50 Gallon (EFBASE) | 0.904 |  | Federal Standard 2004-2014 (based on 50 gallon)
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Electric Resistance Water Heater Existing Efficiency, 50 Gallon (EFBASE) | 0.904 |  | Federal Standard 2004-2014 (based on 50 gallon)
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | R-Value of Unwrapped Tank (RTANK) | 8.3 | °F·ft2·hr/BTU | Pennsylvania 2016 Statewide TRM, Section 2.3.6, Table 2-64
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Surface Area of Unwrapped Water Heater Tank (ABASE) | 23.18 | ft2 | Pennsylvania Statewide TRM, June 2016, Errata Update February 2017,Table 2-63, assumed 40 gallon tank.
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Piping and Insulation Hours of Use (HOU) | 8760 | Hours | Pennsylvania 2015 Statewide TRM, Section 2.3.6, Table 2-60
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Electric Resistance Water Heater Baseline Efficiency, 50 Gallon (EFBASE) | 0.945 | % | Code
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Temperature of Ambient Air (TAMBIENT) | 70 | °F | Pennsylvania 2015 Statewide TRM, Section 2.3.6, Table 2-60
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Surface Area of Wrapped Water Heater Tank (AINSUL) | 25.31 | ft2 | Pennsylvania Statewide TRM, June 2016, Errata Update February 2017,Table 2-63, assumed 40 gallon tank
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Heat Transfer Coefficient of Unwrapped Tank (UBASE) | 0.12048 | BTU/Hr-deg F-ft2 | Calculated from RTANK value
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Heat Transfer Coefficient of Wrapped Tank (UINSUL) | 0.05 | BTU/Hr-deg F-ft2 | Pennsylvania Statewide TRM, June 2016, Errata Update February 2017, Table 2-62 default assumed value
Tank Wrap on Water Heater | Domestic Hot Water | delta_kWh = {[(UTANK x ATANK) - (UINSUL x AINSUL)] x (TWATER - TAMBIENT) / (3412 x EFBASE)} x HOU |  | Temperature of Hot Water Heater (THOT) | 125 | °F | Illinois TRM, Version 5.0,Volume 3: Residential Measures, Final February 11th, 2016; Effective: June 1st, 2016, Section 5.4.2, page 167
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Bi-Level Controls Savings Factor (SVGEE) | 0.31 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Exterior Lighting Energy Use Intensity (EUIExterior Lighting) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Total Lighting Load Connected to Control (kWCONTROLLED) | 0.5 | kW | Measure Definition
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Bi-Level Lighting Control (Exterior) | Exterior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
CFL - 15W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Commercial Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 2.1.1, Table 2-6
CFL - 15W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | CFL 15W Flood Exterior Power of Efficient Lamp (kWEFF) | 15 | W | Measure Definition
CFL - 15W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | CFL 15W Flood Exterior Power of EISA-2020 Compliant Baseline Equipment (kWBASE) | 19.5 | W | Measure Definition
CFL - 15W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient High Bay Lamp/Fixture Type | Ceramic Metal Halide, 400W |  | Measure Definition
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 400W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent High Bay Fixture (kWBASE) | 434.64 | W | "High Bay Light Market Effects Study Final Report for CA PUC" by KEMA & Itron, and Pennsylvania 2016 Statewide TRM, Appendix C
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 1000W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 400W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per High Bay Fixture | 1 |  | Measure Definition
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient High Bay Fixture (kWBASE) | 400 | W | Pennsylvania 2016 Statewide TRM, Appendix C
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Other High Bay Fixture (kWBASE) | 666 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
High Efficiency HID Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent High Bay Fixture (kWBASE) | 403 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED - 9W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
LED - 9W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | LED 9W Flood Exterior Power of Efficient Lamp (kWEFF) | 9 | W | Measure Definition
LED - 9W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | LED 9W Flood Exterior Power of EISA-2020 Compliant Baseline Equipment (kWBASE) | 19.5 | W | Measure Definition
LED - 9W Flood | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Commercial Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 2.1.1, Table 2-6
LED Display Lighting (Exterior) | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Power of Neon or Argon-mercury Signage (kWBASE) | 1.08 | Kw | Pennsylvania 2016 Statewide TRM, Section 3.1.6, Table 3-21
LED Display Lighting (Exterior) | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Power of Efficient LED Signage (kWEFF) | 0.14 | Kw | Pennsylvania 2016 Statewide TRM, Section 3.1.6, Table 3-21
LED Display Lighting (Exterior) | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
LED Display Lighting (Exterior) | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Lumen-Equivalent HID Fixture (kWBASE) | 157 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 100W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 100W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Exterior Lighting Interactive Energy Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Efficient Exterior Lamp/Fixture Type | LED Canopy, 65W |  | Measure Definition
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Efficient Exterior Fixture (kWBASE) | 62
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Incandescent Fixture | Incandescent, 200W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Incandescent Fixture (kWBASE) | 600 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 175W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Exterior Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Quantity of Lamps per Exterior Fixture | 1 |  | Measure Definition
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Exterior Lighting Interactive Energy Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 400W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 200W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 200W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Incandescent Fixture | Incandescent, 500W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Incandescent Fixture (kWBASE) | 1000 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Lumen-Equivalent HID Fixture (kWBASE) | 312.3333 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Efficient Exterior Lamp/Fixture Type | LED, 160W |  | Measure Definition
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Efficient Exterior Fixture (kWEFF) | 160 | W | Pennsylvania 2016 Statewide TRM, Appendix C
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
LED Parking Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Quantity of Lamps per Exterior Fixture | 1 |  | Measure Definition
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 310W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 400W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Incandescent Fixture | Incandescent, 1000W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 1000W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Lumen-Equivalent HID Fixture (kWBASE) | 632.6667 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Efficient Exterior Lamp/Fixture Type | LED, 210W |  | Measure Definition
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Power of Efficient Exterior Fixture (kWEFF) | 211.78 | W | Pennsylvania 2016 Statewide TRM, Appendix C
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Quantity of Lamps per Exterior Fixture | 1 |  | Measure Definition
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
LED Street Lights | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 + IFENERGY)] |  | Exterior Lighting Interactive Energy Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Traffic Signal Controls Savings Factor (SVG) | 0 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.4, Table 3-16
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient Hand/Man Crosswalk Signal (kWEFF) | 0.0073333 | kW | Pennsylvania 2016 Statewide TRM, Section 3.1.4, Table 3-17, All Crosswalk Options
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Hand/Man Crosswalk Signal (kWBASE) | 0.116 | kW | Pennsylvania 2016 Statewide TRM, Section 3.1.4, Table 3-17, All Crosswalk Options
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Baseline Hand/Man Crosswalk Signal (kWBASE) | 0.011667 | kW | ENERGY STAR Criteria
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Exterior Lighting Interactive Energy Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9
LED Traffic and Crosswalk Lighting | Exterior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Crosswalk Signals Hours of Use (HOU) | 8760 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.1.4, Table 3-16
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Dusk-to-Dawn Hours of Use (HOU) | 4018 | Hours | The Civil night time hours - average for multiple Florida cities
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Total Lighting Load Connected to Control (kWCONTROLLED) | 0.5 | kW | Measure Definition
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Exterior Lighting Energy Use Intensity (EUIExterior Lighting) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Photocell Dimming Savings Factor (SVGEE) | 0.28 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Outdoor Lighting Controls | Exterior Lighting | kWh = kWCONTROLLED x HOU x (SVGBASE-SVGEFF) |  | Exterior Code Required Controls Saving Factor (SVGBASE) | 1 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Air Curtains | HVAC | delta_kWh = E_sav | delta_kWh = E_Save | Com Air Curtain Annual Energy Savings (E_Save) | 81 | kWh | AMCA International. Investigation of Impact of Building Entrance Air Curtain on Whole Building Energy Use. Air Curtain Performance on Single Door in Miami.
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Free cooling hours with outdoor temperature between 55 F and 65 F (FCHr_FL Zone2) | 261 | Hours | From TMY3, http://rredc.nrel.gov/solar/old_data/nsrdb/1991-2005/tmy3/by_state_and_city.html#F
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Free cooling hours with outdoor temperature between 55 F and 65 F (FCHr_FL Zone1) | 96 | Hours | From TMY3, http://rredc.nrel.gov/solar/old_data/nsrdb/1991-2005/tmy3/by_state_and_city.html#F
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Savings factor; Annual cooling load savings per unit area of conditioned space in the building when compared with a baseline HVAC system with no economizer (SF) | 0.002 | Ton/ft2 | Pennsylvania Statewide TRM, June 2016, Errata Update February 2017, Section 3.2.9, default value.
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Airside Economizer | HVAC | delta_kWh =[(SF)(Area)(FCHr)(12 Mbh/Ton)]/Eff |  | Average HVAC Efficiency by Building Type (EER) | See Table Below | BTU/W·hr | End-Use Study
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 38 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Baseline Commercial Ceiling Insulation, R-Value (RBASE) | 12 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Insulation Framing Factor (FFRAME) | 0.07 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for wall and attic insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticHeat) | 0.6 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for cooling savings from basement wall insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticCool) | 0.8 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R12 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Seasonal Energy Efficiency Ratio of cooling system (ɳCool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 38 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for wall and attic insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticHeat) | 0.6 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Insulation Framing Factor (FFRAME) | 0.07 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Baseline Commercial Ceiling Insulation, R-Value (RBASE) | 19 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for cooling savings from basement wall insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticCool) | 0.8 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R19 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Seasonal Energy Efficiency Ratio of cooling system (ɳCool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Insulation Framing Factor (FFRAME) | 0.07 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 38 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Baseline Commercial Ceiling Insulation, R-Value (RBASE) | 30 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for wall and attic insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticHeat) | 0.6 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ?Cool) x ADJcooling | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ?Cool) x ADJcooling | Adjustment for cooling savings from basement wall insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticCool) | 0.8 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ?Cool) x ADJcooling | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R30 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ?Cool) x ADJcooling | Seasonal Energy Efficiency Ratio of cooling system (?Cool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for wall and attic insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticHeat) | 0.6 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Baseline Commercial Ceiling Insulation, R-Value (RBASE) | 5 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 38 | °F·ft2·hr/BTU | Measure Definition
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Insulation Framing Factor (FFRAME) | 0.07 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for cooling savings from basement wall insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticCool) | 0.8 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Ceiling Insulation(R2 to R38) | HVAC | delta_kWh = (1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x HDD / (EFF x 3412) x ADJheating | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Seasonal Energy Efficiency Ratio of cooling system (?Cool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Chilled Water Controls Optimization | HVAC | delta_kWh = (delta_TEXISTING-delta_TPROPOSED)*500*Chiller GPM*EFHLCOOL*Chiller_Eff*AreaLoad/12000 |  | Estimated chilled water return temperature - proposed chilled water supply temperature | 17.5 | °F | Engineering Assumption
Chilled Water Controls Optimization | HVAC | delta_kWh = (delta_TEXISTING-delta_TPROPOSED)*500*Chiller GPM*EFHLCOOL*Chiller_Eff*AreaLoad/12000 |  | Chiller GPM | 2 | GPM/ton | Wisconsin Focus on Energy Technical Reference Manual, 2018
Chilled Water Controls Optimization | HVAC | delta_kWh = (delta_TEXISTING-delta_TPROPOSED)*500*Chiller GPM*EFHLCOOL*Chiller_Eff*AreaLoad/12000 |  | Area Load assumed as 0.025 | 0.025 |  | Engineering Assumption
Chilled Water Controls Optimization | HVAC | delta_kWh = (delta_TEXISTING-delta_TPROPOSED)*500*Chiller GPM*EFHLCOOL*Chiller_Eff*AreaLoad/12000 |  | Averaged kw/ton partial load rating (Air-Cooled Chiller/Water-Cooled Chiller) | 0.795 | kw/ton | Wisconsin Focus on Energy Technical Reference Manual, 2018
Chilled Water Controls Optimization | HVAC | delta_kWh = (delta_TEXISTING-delta_TPROPOSED)*500*Chiller GPM*EFHLCOOL*Chiller_Eff*AreaLoad/12000 |  | Estimated chilled water return temperature - existing chilled water supply temperature | 20 | °F | Engineering Assumption
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Annual Hours of Operation (Hours) | 6000 | hrs | Hawaii Energy - TRM No. 2013
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Average motor load (Load_Factor) | 0.75 | % | Hawaii Energy - TRM No. 2011
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Savings factor by using a variable speed drive (Savings_Factor) | 0.2474 | % | Hawaii Energy - TRM No. 2011
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Motor efficiency (Eff) | 0.92 | % | Hawaii Energy - TRM No. 2012
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Chilled Water System - Variable Speed Drives | HVAC | delta_kWh = HP x 0.746 x Load_Factor/Eff x Hours x Savings_Factor |  | Chilled water pump horsepower (HP) | 10 | hp | Hawaii Energy - TRM No. 2011
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Efficiency of Heating System (Electric) (EFF) | 0.8 | % | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Annual Cooling Load for a standard black roof (HeatingLoad_Black) | 1505 | Btu/ft2 | Oak Ridge National Laboratory. Cool Roof Calculator for Tampa, Florida
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Coof Roof Insulated Area (A) | 15707 | ft2 | Enegineering assumption - typical commercial space
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Annual Cooling Load for an energy efficient cool roof (HeatingLoad_EE) | 1459 | Btu/ft2 | Oak Ridge National Laboratory. Cool Roof Calculator for Tampa, Florida
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Annual Cooling Load for a standard black roof (CoolingLoad_Black) | 6847 | Btu/ft2 | Oak Ridge National Laboratory. Cool Roof Calculator for Tampa, Florida
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Annual Cooling Load for an energy efficient cool roof (CoolingLoad_EE) | 4591 | Btu/ft2 | Oak Ridge National Laboratory. Cool Roof Calculator for Tampa, Florida
Cool Roof | HVAC | delta_kWh = [(HeatingLoad_Base - HeatingLoad_EE) x Area ] x 0.000293071 / EFF | delta_kWh = [(CoolingLoad_Base - CoolingLoad_EE) x Area ] / 1,000 / EER | Cooling energy efficiency ratio (EER) | 11 | kBtu/kWh | ASHRAE 90.1 Air-cooled AC unit >135 kBTU/h
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Capacity (Tons) | 4 | Tons | Measure Definition
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Heating Seasonal Performance Factor Baseline (HSPF_Base) | 6.6 | BTU/W-hr | 2006 IECC, Table 503.2.3 (2)
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | DOAS_Heat_Savings | 0.9 | % | US Department of Energy
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Heating Seasonal Performance Facotr High Efficiency (HSPF_Eff) | 9.6 | BTU/W-hr | AHRI Database, Average 4 Ton Unit
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Baseline Efficiency (SEE_Base) | 10.1 | BTU/W-hr | IECC 2012
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump High Efficiency (SEER_Eff) | 16 | BTU/W-hr | AHRI Database, Average 4 Ton Unit
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours
Dedicated Outdoor Air System on VRF unit | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | DOAS_Cool_Savings | 0.825 | % | US Department of Energy
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Existing Commercial Construction, wall R value (combasewallr) | 6.5 | °F·ft2·hr/BTU | Illinois Statewide Technical Reference Manual, Feb 11, 2016
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | New Commercial Construction, roof R value (comnewroofr) | 20 | °F·ft2·hr/BTU | Illinois Statewide Technical Reference Manual, Feb 11, 2016
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Existing Commercial Construction, roof R value (combaseroofr) | 10 | °F·ft2·hr/BTU | Measure Definition
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | New Commercial Construction, wall R value (comnewwallr) | 13 | °F·ft2·hr/BTU | Illinois Statewide Technical Reference Manual, Feb 11, 2016
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Average Premise Number of Floors (NFLOORS) | See Table Below |  | End-Use Study
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Fan input power (kW) | 0.25 | Kw | http://www.reznorhvac.com/files/Maximizor_destratification_fan_En_2012-07.pdf
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Temperature set point at the thermostat (Ttstat) | 68 | °F | Engineering Assumption
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Number of fans (Nfan) | 1 |  | Engineering Assumption
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Thermal Efficiency of heating equipment | 0.8 |  | Illinois Statewide Technical Reference Manual, Feb 11, 2016
Destratification Fans | HVAC | delta_kWh = [(delta_Qr + delta_Qw) * teff] / (100,000 * ɳ) * (29.31kWh/therm) - ((Wfan * Nfan) * teff) |  | Assumed ceiling height/roof deck (ft) | 30 | ft | Engineering Assumption
Duct Insulation | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Duct Insulation Energy Savings Factor (SVGE) | 0.020453 | % | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix D
Duct Insulation | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Duct Insulation | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Duct Insulation | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Duct Sealing Repair | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Duct Sealing Energy Savings Factor (SVGE) | 0.12 | % | Regional Technical Forum - Residential: Heating/Cooling - Duct Sealing SF V2.0
Duct Sealing Repair | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Duct Sealing Repair | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Duct Sealing Repair | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
ECM Motors on Furnaces | HVAC | delta_kWh = CAP x 12 x SVF x EFLH_Heat |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
ECM Motors on Furnaces | HVAC | delta_kWh = CAP x 12 x SVF x EFLH_Heat |  | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below | Hours | End-Use Study
ECM Motors on Furnaces | HVAC | delta_kWh = CAP x 12 x SVF x EFLH_Heat |  | Furnace capacity (CAP) | 0.15 | MMBTU | Measure Definition
ECM Motors on Furnaces | HVAC | delta_kWh = CAP x 12 x SVF x EFLH_Heat |  | Annual kWh savings per MMBtu of heating fuel consumption (SVF) | 5 | kWh/MMBTU | Adapted from “Electricity Use by New Furnaces: A Wisconsin Field Study,” Energy Center of Wisconsin, 10/2003. Assumes ECM fan motor savings scale linearly with annual fuel consumption.
ECM Motors on Furnaces | HVAC | delta_kWh = CAP x 12 x SVF x EFLH_Heat |  | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Energy Recovery Ventilation System (ERV) | HVAC | ΔkWh = EUI_space cooling x AREA x SVGE |  | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Energy Recovery Ventilation System (ERV) | HVAC | ΔkWh = EUI_space cooling x AREA x SVGE |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Energy Recovery Ventilation System (ERV) | HVAC | ΔkWh = EUI_space cooling x AREA x SVGE |  | Energy Recovery Ventilation Energy Savings Factor (SVGE) | See Table Below | % | FPL Technical Primer - Energy Recovery Ventilation
Facility Commissioning | HVAC | delta_kWh = EUIAll x AREA x SVGE |  | Retrocommissioning Energy Savings Factor (SVGE) | 0.16 | % | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Facility Commissioning | HVAC | delta_kWh = EUIAll x AREA x SVGE |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Facility Commissioning | HVAC | delta_kWh = EUIAll x AREA x SVGE |  | All Energy Use Intensity (EUIAll) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Facility Energy Management System | HVAC | delta_kWh = EUI x AREA x SVG |  | Facility Energy Management Energy Savings Factor for HVAC (SVGE) | 0.2 | % | Engineering Assumption
Facility Energy Management System | HVAC | delta_kWh = EUI x AREA x SVG |  | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Facility Energy Management System | HVAC | delta_kWh = EUI x AREA x SVG |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Facility Energy Management System | HVAC | delta_kWh = EUI x AREA x SVG |  | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Baseline Commercial Floor Insulation, R-Value (RBASE) | 13 | °F·ft2·hr/BTU | IECC 2012
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 19 | °F·ft2·hr/BTU | Measure Definition
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Efficiency of Heating System (Electric) (EFF) | 0.8 | % | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Insulation Framing Factor (FFRAME) | 0.15 | % | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Adjustment for wall and attic insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticHeat) | 0.6 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Cooling energy efficiency ratio (EER) | 11 | kBtu/kWh | ASHRAE 90.1 Air-cooled AC unit >135 kBTU/h
Floor Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | Electric Heat Coefficient of Performance Baseline (COP_Base) | 3.3 | BTU/W-hr | IECC 2012
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | Geothermal Heat Pump Capacity (Tons) | 10 | Tons | Measure Definition
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | Electric Heat Coefficient of Performance High Efficiency (COP_Eff) | 3.4 | BTU/W-hr | ASHRAE 90.1-2007
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | HSPF_Eff | 11.6008 | BTU/W-hr | Calculated from COP
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | HSPF_Base | 11.2596 | BTU/W-hr | Calculated from COP
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below | Hours | 0
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | Geothermal Heat Pump Baseline Efficiency (EER_Base) | 13.4 | BTU/W-hr | ASHRAE 90.1-2010 Table 6.8.1B
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | Geothermal Heat Pump High Efficiency (EER_Eff) | 17 | BTU/W-hr | Engineering Assumption
Geothermal Heat Pump | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/EERBASE - 1/EEREFF) | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Efficient Commercial Ceiling Insulation, R-Value (R_Base) | 27.5 | °F·ft2·hr/BTU | Evaluating Green Roof Energy Performance. ASHRAE Journal February 2006. Article stated insulation of the green roof ranged from 17 to 38. Assumed average value.
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Green Roof Insulated Area (A) | 15707 | ft2 | Enegineering assumption - typical commercial space
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Efficiency of Heating System (Electric) (EFF) | 0.8 | %
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Baseline Commercial Ceiling Insulation, R-Value (R_Base) | 15 | °F·ft2·hr/BTU | Insulation required per ASHRAE 90.1 for Insulation Entirely above Deck
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Insulation Framing Factor (R_Frame) | 0.15 | - | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Cooling energy efficiency ratio (EER) | 11 | kBtu/kWh | ASHRAE 90.1 Air-cooled AC unit >135 kBTU/h
Green Roof | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh = [(1/R_Base - 1/R_Eff) x Area x (1 - F_Frame) x 24 x CDD x DUA] / 1,000 / EER | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
High Efficiency Chiller (Air Cooled, 50 tons) | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air Cooled Chiller, <150 Tons, Minimum EER (EERBASE) | 12.5 | BTU/W·hr | Code
High Efficiency Chiller (Air Cooled, 50 tons) | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air Cooled Chiller, <150 Tons, Existing EER (EERBASE) | 9.5536 | BTU/W·hr | 2006 IECC, Table 503.2.3 (7)
High Efficiency Chiller (Air Cooled, 50 tons) | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air Cooled Chiller, <150 Tons, Efficient EER (EEREFF) | 13.7 | BTU/W·hr | ASHRAE 189.1-2014 Path A, Part Load
High Efficiency Chiller (Air Cooled, 50 tons) | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency Chiller (Air Cooled, 50 tons) | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Capacity (TONS) | 50 | Tons | Measure Definition
High Efficiency Chiller (Water cooled-centrifugal, 200 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Centrifugal, <300 Tons, Minimum IPLV (IPLVBASE) | 0.596 | kW/Ton | Code
High Efficiency Chiller (Water cooled-centrifugal, 200 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Centrifugal, <300 Tons, Efficient IPLV (IPLVEFF) | 0.57 | kW/Ton | Assumed 5% better than code
High Efficiency Chiller (Water cooled-centrifugal, 200 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency Chiller (Water cooled-centrifugal, 200 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Centrifugal, <300 Tons, Existing IPLV (IPLVBASE) | 0.596 | kW/Ton | ASHRAE 90.1 before 1/1/2010
High Efficiency Chiller (Water cooled-centrifugal, 200 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Capacity (TONS) | 200 | Tons | Measure Definition
High Efficiency Chiller (Water cooled-positive displacement, 100 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Capacity (TONS) | 100 | Tons | Measure Definition
High Efficiency Chiller (Water cooled-positive displacement, 100 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Positive Displacement, <75 Tons, Existing IPLV (IPLVBASE) | 0.676 | kW/Ton | ASHRAE 90.1 before 1/1/2010
High Efficiency Chiller (Water cooled-positive displacement, 100 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency Chiller (Water cooled-positive displacement, 100 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Positive Displacement, <150 Tons, Minimum IPLV (IPLVBASE) | 0.615 | kW/Ton | Code
High Efficiency Chiller (Water cooled-positive displacement, 100 tons) | HVAC | delta_kWh = TONS x (IPLVBASE - IPLVEFF) x EFLHCOOL |  | Water Cooled, Positive Displacement, <75 Tons, Efficient IPLV (IPLVBASE) | 0.5985 | kW/Ton | Assumed 5% better than code
High Efficiency Data Center Cooling | HVAC | delta_kWh = (HEDC_Avg_Baseline_kW - HEDC_Avg_Eff_kW)*Hours per year |  | HEDC_Avg_Eff_kW | 297.5 | kw | Minnesota TRM
High Efficiency Data Center Cooling | HVAC | delta_kWh = (HEDC_Avg_Baseline_kW - HEDC_Avg_Eff_kW)*Hours per year |  | HEDC_Avg_Baseline_kW | 482 | kw | Minnesota TRM
High Efficiency Data Center Cooling | HVAC | delta_kWh = (HEDC_Avg_Baseline_kW - HEDC_Avg_Eff_kW)*Hours per year |  | Hours per year | 8760 | hours
High Efficiency DX 135k- less than 240k BTU_h Other Heat | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air-Cooled AC, <240,000 BTU, Efficient EER (EERBASE) | 11.5 | BTU/W·hr | AHRI Database, Average 15 Ton Unit
High Efficiency DX 135k- less than 240k BTU_h Other Heat | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency DX 135k- less than 240k BTU_h Other Heat | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air-Cooled AC, All Other, <240,000 BTU, Existing EER (EERBASE) | 9.3 | BTU/W·hr | 2006 IECC, Table 503.2.3 (2)
High Efficiency DX 135k- less than 240k BTU_h Other Heat | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Capacity (TONS) | 15 | Tons | Measure Definition
High Efficiency DX 135k- less than 240k BTU_h Other Heat | HVAC | delta_kWh = TONS x 12 x [(1/EERBASE) - (1/EEREFF)] x EFLHCOOL |  | Air-Cooled AC, All Other, <240,000 BTU, Minimum EER (EERBASE) | 10.8 | BTU/W·hr | Code
High Efficiency PTAC | HVAC | delta_kWh = Tons x 12 x (1/SEER_Base - 1/SEER_Eff) x EFLH_Cool |  | PTAC/PTHP Capacity (Tons) | 1.5 | Tons | AHRI Database, Average Tonnage
High Efficiency PTAC | HVAC | delta_kWh = Tons x 12 x (1/SEER_Base - 1/SEER_Eff) x EFLH_Cool |  | PTAC, Cooling Mode, 1-2 Ton, Replacements (EERBASE) | 7.1 | BTU/W·hr | Code
High Efficiency PTAC | HVAC | delta_kWh = Tons x 12 x (1/SEER_Base - 1/SEER_Eff) x EFLH_Cool |  | PTAC, Efficient SEER (SEEREFF) | 11 | BTU/W·hr | AHRI Database, Average 1 - 2 Ton Unit
High Efficiency PTAC | HVAC | delta_kWh = Tons x 12 x (1/SEER_Base - 1/SEER_Eff) x EFLH_Cool |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency PTAC | HVAC | delta_kWh = Tons x 12 x (1/SEER_Base - 1/SEER_Eff) x EFLH_Cool |  | PTAC, Cooling Mode, 1-2 Ton, New Construction (EERBASE) | 8.4 | BTU/W·hr | Code
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | New Construction HSPF_Base | 10.9184 | BTU/W·hr | Calculated from COP
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | PTAC/PTHP Capacity (Tons) | 1.5 | Tons | AHRI Database, Average Tonnage
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | PTHP, Cooling Mode, 1-2 Ton, New Construction (EERBASE) | 8.6 | BTU/W·hr | Code
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Replacements HSPF_Base | 9.8948 | BTU/W·hr | Calculated from COP
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below | Hours | End-Use Study
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Efficient HSPF_Eff | 10.9184 | BTU/W·hr | Calculated from COP
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | PTHP, Efficient SEER (SEEREFF) | 11 | BTU/W·hr | AHRI Database, Average 1 - 2 Ton Unit
High Efficiency PTHP | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | PTHP, Cooling Mode, 1-2 Ton, Replacements (EERBASE) | 7 | BTU/W·hr | Code
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Capacity (TONS) | 3 | Tons | Measure Definition
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Average Hotel Key Card Room ECS Energy Savings (SVGE) | 187.14 | kwh/ton | Averaged from IL TRM v4.0 pg 198-200
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Average Hotel Key Card Room ECS Demand Savings (SVGD) | 0.0816 | kw/ton | Averaged from IL TRM v4.0 pg 198-200
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Hotel Card Energy Control Systems | HVAC | delta_kWh = SVGE x TONS | delta_kWh = SVGE x TONS | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below | Hours | End-Use Study
HVAC tune-up | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | Percent improvement based on measured EERs pre- and post-tune-up ( %_impr) | 0.05 | % | Energy Center of Wisconsin, May 2008; “Central Air Conditioning in Wisconsin, A Compilation of Recent Field Research.”
HVAC tune-up | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | PTAC/PTHP Capacity (Tons) | 1.5 | Tons | AHRI Database, Average Tonnage
HVAC tune-up | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | PTAC, Cooling Mode, 1-2 Ton (EERBASE) | 8.4 | BTU/W·hr | Code
HVAC tune-up | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
HVAC tune-up_RTU | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | Air-Cooled AC, Electric Resistance, <135,000 BTU, Minimum EER (EERBASE) | 11.2 | BTU/W∙hr | Code
HVAC tune-up_RTU | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | Percent improvement based on measured EERs pre- and post-tune-up (SVGE) | 0.05 | % | Energy Center of Wisconsin, May 2008; “Central Air Conditioning in Wisconsin, A Compilation of Recent Field Research.”
HVAC tune-up_RTU | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | Capacity (TONS) | 10 | Tons | Measure Definition
HVAC tune-up_RTU | HVAC | delta_kWh = Tons x 12 x 1/EER_base x EFLH_Cool x SVGE |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Reduction in infiltration in CFM (CFM_red) | 1000 | CFM | Assumed
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | volumetric heat capacity of air (rho_air) | 0.018 | Btu/ft3 | standard value
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | conversion from CFM50 to CFM_Natural (N_factor) | 20 | - | Assumed N-Factor for a normal exposure. N-factor is used to convert 50-pascal blower door air flows to natural air flows and is dependent on geographic location and exposure of the home to wind, based on methodology developed by Lawrence Berkel
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Efficiency of Heating System (Electric) (EFF) | 0.8 | % | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Infiltration Reduction - Air Sealing | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Cooling energy efficiency ratio (EER) | 11 | kBtu/kWh | ASHRAE 90.1 Air-cooled AC unit >135 kBTU/h
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Baseline Commercial Fenestration, U-Value (UBASE) | See Table Below | BTU/°F·ft2·hr | IECC 2012
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Insulated Area (A) | 100 | ft2 | Measure Definition
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Energy Star Window U-Value (UEFF) | 0.27 |  | Energy Star Qualification Criteria for Windows V6.0
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Existing Window U-Value (UBASE) | 0.3 |  | Energy Star Qualification Criteria for Windows V5.0
Low U-Value Windows | HVAC | delta_kWh = {[(UBASE - 1/REFF) x A x 24 x CDD / EFF] / 1,000,000 x 293.07} | delta_kWh = [(U_Base - 1/R_Eff) x A x 24 x HDD / EFF x 0.000293071] | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Programmable Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Programmable Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Programmable Thermostat Savings Factor (SVGE) | 0.036 | % | Pennsylvania 2016 Statewide TRM, Section 2.2.8, Table 4-21
Programmable Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Programmable Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficient Commercial Ceiling Insulation, R-Value (REFF) | 30 | °F·ft2·hr/BTU | Measure Definition
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Baseline Commercial Ceiling Insulation, R-Value (RBASE) | 15 | °F·ft2·hr/BTU | Measure Definition
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Efficiency of Heating System (EFF) | 1.92 |  | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Insulation Framing Factor (FFRAME) | 0.15 | - | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Adjustment for cooling savings from basement wall insulation to account for prescriptive engineering algorithms overclaiming savings (ADJwallAtticCool) | 0.8 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Roof Insulation | HVAC | delta_kWh = [(1/R_Base - 1/R_Eff) x A x (1 - F_Frame) x 24 x HDD / EFF] x 0.000293071 | delta_kWh =[(1/RBASE - 1/REFF) x A x (1 - FFRAME) x 24 x CDD x DUA ]/ (1000 x ɳCool) x ADJcooling | Seasonal Energy Efficiency Ratio of cooling system (ɳCool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Smart Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Smart Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Smart Thermostat Savings Factor (SVGE) | 0.1 | % | Vectren 2013-14 Nest Pilot Program Evaluation
Smart Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Smart Thermostat | HVAC | delta_kWh = EUI x AREA x SVG | delta_kWh = EUI x AREA x SVG | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Heating Hours (EFLHHEAT) | See Table Below | Hours | 0
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Capacity (Tons) | 4 | Tons | Measure Definition
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Heating Seasonal Performance Facotr High Efficiency (HSPF_Eff) | 9.6 | BTU/W-hr | AHRI Database, Average 4 Ton Unit
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Heating Seasonal Performance Factor Baseline (HSPF_Base) | 6.6 | BTU/W-hr | 2006 IECC, Table 503.2.3 (2)
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump Baseline Efficiency (SEE_Base) | 10.1 | BTU/W-hr | IECC 2012
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | Heat Pump High Efficiency (SEER_Eff) | 16 | BTU/W-hr | AHRI Database, Average 4 Ton Unit
Variable Refrigerant Flow (VRF) HVAC Systems | HVAC | delta_kWh = Tons x 12 x (1/HSPF_Base - 1/HSPF_Eff) x EFLH_Heat | delta_kWh = TONS x EFLHCOOL x 12 x (1/SEERBASE - 1/SEEREFF) | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | FL Zone 2, Baseline Commercial Above-Grade Wall Insulation, U-Value (UBASE) | 0.077 | BTU/°F·ft2·hr | Measure Definition
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Average Premise Number of Floors (NFLOORS) | See Table Below |  | End-Use Study
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Discretionary Use Adjustment (DUA) | 0.75 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Existing Commercial Below-Grade Wall Insulation, R-Value (RBASE) | See Table Below | °F·ft2·hr/BTU | End-Use Study
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | FL Zone 1, Baseline Commercial Above-Grade Wall Insulation, U-Value (UBASE) | 0.077 | BTU/°F·ft2·hr | Code
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Insulation Framing Factor (FFRAME) | 0.07 | % | Illinois TRM Version 6.0, Volume 3: Residential Measures, 5.6.4 Wall and Ceiling/Attic Insulation
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Seasonal Energy Efficiency Ratio of cooling system (ɳCool) | 13 | kBtu/kWh | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Assumed House Height | 8 | ft | Engineering Assumption
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Efficient Commercial Above-Grade Wall Insulation, R-Value (REFF) | 12.987 | °F·ft2·hr/BTU | Measure Definition
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Adjustment for wall insulation (ADJWall) | 0.63 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 3.0
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Efficiency of heating system (ɳHeat) | 1.92 |  | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 3.0
Wall Insulation | HVAC | delta_kWh = [((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) + (1/R_old - 1/R_attic) *A_attic * (1-Framing_factor_attic)) * 24 * CDD * DUA] / (1000 * ɳCool) | delta_kWh = (((1/R_old - 1/R_wall) * A_wall * (1-Framing_factor_wall) * ADJWall ) + (1/R_old - 1/R_attic) * A_attic * (1-Framing_factor_attic) * ADJAttic) * 24 * HDD] / (ɳHeat * 3412) | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Heating Degree Days (HDD) | See Table Below |  | ASHRAE 90.1
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | volumetric heat capacity of air (rho_air) | 0.018 | Btu/ft3 | standard value
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Efficiency of Heating System (Electric) (EFF) | 0.8 | % | Minnesota 2016 Statewide TRM V1.3, Residential Insulation & Air Sealing V1.3
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | conversion from CFM50 to CFM_Natural (N_factor) | 20 | - | Assumed N-Factor for a normal exposure. N-factor is used to convert 50-pascal blower door air flows to natural air flows and is dependent on geographic location and exposure of the home to wind, based on methodology developed by Lawrence Berkel
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Reduction in infiltration in CFM (CFM_red_warehouse) | 2000 | CFM | Engineering Assumption
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Cooling Degree Days (CDD) | See Table Below |  | ASHRAE 90.1
Warehouse Loading Dock Seals | HVAC | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x HDD x rho_air ] / EFF x 0.000293071 | delta_kWh = [(CFM_red/N_factor) x 60 x 24 x CDD x rho_air ] / 1,000 / EER | Cooling energy efficiency ratio (EER) | 11 | kBtu/kWh | ASHRAE 90.1 Air-cooled AC unit >135 kBTU/h
Water Cooled Refrigeration Heat Recovery | HVAC | delta_kWh = kWhbase * SVG |  | Water Cooled Refrigeration Heat Recovery Energy Savings Factor (SVGE) | 0.1 | % | Engieering Assumption
Water Cooled Refrigeration Heat Recovery | HVAC | delta_kWh = kWhbase * SVG |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Water Cooled Refrigeration Heat Recovery | HVAC | delta_kWh = kWhbase * SVG |  | Space Heating Energy Use Intensity (EUISpace Heating) | See Table Below | kWh/ft2/yr | Gulf UEC data
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Water Cooled, Centrifugal, <300 Tons, Minimum IPLV (IPLVBASE) | 0.596 | kW/Ton | Code
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Capacity (TONS) | 200 | Tons | Measure Definition
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Free cooling hours with outdoor wetbulb temperature between 35 and 50F (FCHr FL Zone 2) | 145 | hours | https://www.energystar.gov/products/low_carbon_it_campaign/12_ways_save_energy_data_center/water_side_economizer
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Free cooling hours with outdoor wetbulb temperature between 35 and 50F (FCHr FL Zone 1) | 34 | hours | https://www.energystar.gov/products/low_carbon_it_campaign/12_ways_save_energy_data_center/water_side_economizer
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Water Cooled, Centrifugal, <300 Tons, Existing IPLV (IPLVBASE) | 0.596 | kW/Ton | ASHRAE 90.1 before 1/1/2010
Waterside Economizer | HVAC | kWh = (Ton)(IPLV)(EFLH)(FCHr)/(CH) |  | Annual Cooling Hours according to FCHr schedule, ie 8am-6pm, M-F (CH) | 2610 | hrs/yr
Window Sun Protection | HVAC | delta_kWh =CAPY x (1/EER) x EFLHCOOL x (SHGCBASE-SHGCEFF) |  | Average HVAC Efficiency by Building Type (EER) | See Table Below | BTU/W·hr | End-Use Study
Window Sun Protection | HVAC | delta_kWh =CAPY x (1/EER) x EFLHCOOL x (SHGCBASE-SHGCEFF) |  | Existing Commercial Windows, SHGC (SHGCBASE) | 0.25 | % | IECC 2012
Window Sun Protection | HVAC | delta_kWh =CAPY x (1/EER) x EFLHCOOL x (SHGCBASE-SHGCEFF) |  | Window Shade Film SHGC (SHGCEFF) | 0.21 | % | Measure Definition
Window Sun Protection | HVAC | delta_kWh =CAPY x (1/EER) x EFLHCOOL x (SHGCBASE-SHGCEFF) |  | Average HVAC Capacity by Building Type (CAPY) | See Table Below | Btu/hr | Engineering assumption
Window Sun Protection | HVAC | delta_kWh =CAPY x (1/EER) x EFLHCOOL x (SHGCBASE-SHGCEFF) |  | HVAC Effective Full Load Cooling Hours (EFLHCOOL) | See Table Below | Hours | End-Use Study
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Bi-Level Controls Savings Factor (SVGEE) | 0.31 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Interior Lighting Energy Use Intensity (EUIInterior Lighting) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Bi-Level Lighting Control (Interior) | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Total Lighting Load Connected to Control (kWCONTROLLED) | 0.5 | kW | Measure Definition
CFL-23W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
CFL-23W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | CFL 23W Power of EISA-2020 Compliant Baseline Equipment (kWBASE) | 30 | W | Measure Definition
CFL-23W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Commercial Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 2.1.1, Table 2-6
CFL-23W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | CFL 23W Power of Efficient Lamp (kWEFF) | 23 | W | Measure Definition
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent High Bay Fixture (kWBASE) | 200.91 | W | "High Bay Light Market Effects Study Final Report for CA PUC" by KEMA & Itron, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Other High Bay Fixture (kWBASE) | 312.3333 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per High Bay Fixture | 4 |  | Measure Definition
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 400W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient High Bay Fixture (kWEFF) | 112 | W | Market Research
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 200W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient High Bay Lamp/Fixture Type | T5, High Output, 54W |  | Measure Definition
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent High Bay Fixture (kWBASE) | 186 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 200W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay Fluorescent (T5) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per High Bay Fixture | 1 |  | Measure Definition
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent High Bay Fixture (kWBASE) | 307.74 | W | "High Bay Light Market Effects Study Final Report for CA PUC" by KEMA & Itron, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Other High Bay Fixture (kWBASE) | 578.3333 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Metal Halide Fixture | Pulse Start Metal Halide, 320W |  | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent High Bay Fixture (kWBASE) | 288 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent High Pressure Sodium Fixture | High Pressure Sodium, 250W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lumen Equivalent Mercury Vapor Fixture | Mercury Vapor, 1000W | 0 | Used Lumen Equivalence Calculations to Select Appropriate Fixture Type for Comparison
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient High Bay Lamp/Fixture Type | LED High Bay |  | Measure Definition
High Bay LED | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient High Bay Fixture (kWEFF) | 150 | W | Pennsylvania 2016 Statewide TRM, Appendix C
Interior Lighting Controls | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Interior Lighting Controls | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Photocell Dimming Savings Factor (SVGEE) | 0.28 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Interior Lighting Controls | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
Interior Lighting Controls | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
Interior Lighting Controls | Interior Lighting | delta_kWh = kWCONTROLLED x HOU x (SVGEFF - SVGBASE) x (1 + IFENERGY)] |  | Total Lighting Load Connected to Control (kWCONTROLLED) | 0.5 | kW | Measure Definition
LED - 14W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | LED 14W Power of Efficient Lamp (kWEFF) | 14 | W | Measure Definition
LED - 14W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | LED 14W Power of EISA-2020 Compliant Baseline Equipment (kWBASE) | 30 | W | Measure Definition
LED - 14W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
LED - 14W | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) / 1000 |  | Commercial Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 2.1.1, Table 2-6
LED Display Lighting (Interior) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Power of Efficient LED Signage (kWEFF) | 0.14 | Kw | Pennsylvania 2016 Statewide TRM, Section 3.1.6, Table 3-21
LED Display Lighting (Interior) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
LED Display Lighting (Interior) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Power of Neon or Argon-mercury Signage (kWBASE) | 1.08 | Kw | Pennsylvania 2016 Statewide TRM, Section 3.1.6, Table 3-21
LED Display Lighting (Interior) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Power of Neon or Argon-mercury Signage (kWBASE) | 1.08 | Kw | Pennsylvania 2016 Statewide TRM, Section 3.1.6, Table 3-21
LED Display Lighting (Interior) | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x HOU x (1 + IFENERGY) |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
LED Exit Sign | Interior Lighting | delta_kWh = (kWBASE - kWEFF) / 1000 x [HOU x (1 + IFENERGY)] |  | Exit Sign Hours of Use (HOU) | 8760 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.1.5, Table 3-19
LED Exit Sign | Interior Lighting | delta_kWh = (kWBASE - kWEFF) / 1000 x [HOU x (1 + IFENERGY)] |  | Power of LED Exit Sign (kWEFF) | 5 | W | Pennsylvania 2016 Statewide TRM, Appendix C
LED Exit Sign | Interior Lighting | delta_kWh = (kWBASE - kWEFF) / 1000 x [HOU x (1 + IFENERGY)] |  | Power of Existing Exit Sign (kWBASE) | 16 | W | Pennsylvania 2014 Statewide Act 129 Non-Residential End Use & Saturation Study
LED Exit Sign | Interior Lighting | delta_kWh = (kWBASE - kWEFF) / 1000 x [HOU x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
LED Exit Sign | Interior Lighting | delta_kWh = (kWBASE - kWEFF) / 1000 x [HOU x (1 + IFENERGY)] |  | Power of Baseline Exit Sign (kWBASE) | 9 | W | Pennsylvania Statewide Act 129 2014 Baseline and End-Use Study Report
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per Linear Fluorescent Fixture | 1 |  | Measure Definition
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient Linear Fluorescent Lamp/Fixture Type | CREE LED Troffer |  | Measure Definition
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 28.7247 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 56.32 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient Linear Fluorescent Fixture (kWBASE) | 21 | W | Pennsylvania 2016 Statewide TRM, Appendix C
LED Linear - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient Linear Fluorescent Fixture (kWBASE) | 21 | W | Pennsylvania 2016 Statewide TRM, Appendix C
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per Linear Fluorescent Fixture | 1 |  | Measure Definition
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient Linear Fluorescent Lamp/Fixture Type | CREE Linear LED |  | Measure Definition
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 28.16 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 28.7247 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
LED Linear - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient Linear Fluorescent Lamp/Fixture Type | 4' 28W T8 |  | Measure Definition
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 84.48 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient Linear Fluorescent Fixture (kWBASE) | 73.92 | W | Pennsylvania 2016 Statewide TRM, Appendix C
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 86.1742 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per Linear Fluorescent Fixture | 3 |  | Measure Definition
Premium T8 - Fixture Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 84.48 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Efficient Linear Fluorescent Lamp/Fixture Type | 4' 28W T8 |  | Measure Definition
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Unknown Heating Type Energy Interactive Factor (IFENERGY) | 0 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-9, "Unknown Heating Type"
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Code Required Controls Saving Factor (SVGBASE) | See Table Below | % | End-Use Study
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Quantity of Lamps per Linear Fluorescent Fixture | 3 |  | Measure Definition
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Efficient Linear Fluorescent Fixture (kWEFF) | 73.92 | W | Pennsylvania 2016 Statewide TRM, Appendix C
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Lighting Hours of Use (HOU) | See Table Below | Hours | Indiana TRM Version 2.1, July 15, 2015
Premium T8 - Lamp Replacement | Interior Lighting | delta_kWh = (kWBASE - kWEFF) x [HOU x (1 - SVGBASE) x (1 + IFENERGY)] |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 86.1742 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | Conversion from kilowatts to watts (WHperKWH) | 1000 | Wh/kWh | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | annual hours system is actively charging (hourscharge) | 3942 | hours | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | wattage draw of the system operating with no load or in maintenance mode (Widlepre) | 50 | W | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | wattage draw of the charging system in active charging mode (Wchargepre) | 2000 | W | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | wattage draw of the system with no load or in maintenance mode (Widlepost) | 10 | W | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | annual hours the system is operating with no load or in maintenance mode (hoursidle) | 4818 | hours | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Battery Charger | Miscellaneous | delta_kWh =[hourscharge (Wchargepre -Wchargepost)+hoursidle(Widlepre-Widlepost)]/WHperKWH |  | wattage draw of the charging system in active charging mode (Wchargepost) | 1767 | W | Arkansas TRM Version7.0, Section 3.7.14. TRM Reference: Battery Charger California Title 20 CASE, Analysis of Standard Options for Battery Charger Systems.
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | 5 HP, Existing ODP Motor Efficiency, Assumed 4-Poles (EFFBASE) | 0.875 | 0 | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | Rated Motor Horsepower (HP) | 5 | HP | Measure Definition
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | 5 HP, Efficient ODP Motor Efficiency, Assumed 4-Poles (EFFEFF) | 0.905 | 0 | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | Standard Motor Load Factor (LF) | 0.75 | % | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | 5 HP, Baseline ODP Motor Efficiency, Assumed 4-Poles (EFFBASE) | 0.895 | 0 | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | Efficiency of Synchronous Belt (EFFBELT,EFF) | 0.98 | % | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | Efficiency of Standard V-Belt (EFFBELT,BASE) | 0.93 | 0 | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Efficient Motor Belts | Miscellaneous | delta_kWh = 0.746 x HP x (LF/EFFBASE) x RHRS x [1 - (EFFBELT,BASE / EFFBELT,EFF)] |  | 5 HP Motor Annual Run Hours (RHRS) | 2745 | Hours | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
ENERGY STAR Commercial Clothes Washer | Miscellaneous | delta_kWh= [(CAPbase/MEFb) - (CAPee/MEFp)]*N |  | Capacity of baseline clothes washer (Capbase) | 2.84 | ft3 | California Energy Commission (“CEC”) Appliance Efficiency database, http://www.appliances.energy.ca.gov/QuickSearch.aspx
ENERGY STAR Commercial Clothes Washer | Miscellaneous | delta_kWh= [(CAPbase/MEFb) - (CAPee/MEFp)]*N |  | Number of cycles per year (N) | 2190 | cycles/year | Pennsylvania Statewide TRM, June 2016: U.S. Department of Energy. Commercial Clothes Washer Supplemental Notice of Proposed Rulemaking, Chapter 6.
ENERGY STAR Commercial Clothes Washer | Miscellaneous | delta_kWh= [(CAPbase/MEFb) - (CAPee/MEFp)]*N |  | Capacity of efficient clothes washer (Capee) | 2.84 | ft3 | California Energy Commission (“CEC”) Appliance Efficiency database, http://www.appliances.energy.ca.gov/QuickSearch.aspx
ENERGY STAR Commercial Clothes Washer | Miscellaneous | delta_kWh= [(CAPbase/MEFb) - (CAPee/MEFp)]*N |  | Modified Energy Factor of ENERGY STAR Washing Machine (MEFp) | 2.2 |  | ENERGY STAR. U.S. EPA and U.S. DoE. “ENERGY STAR Program Requirements Product Specification for Clothes Washers.” V6.1 Clothes Washers Specification (Jan. 2013)
ENERGY STAR Commercial Clothes Washer | Miscellaneous | delta_kWh= [(CAPbase/MEFb) - (CAPee/MEFp)]*N |  | Base Federal Standard Modified Energy Factor (MEFb) | 1.6 |  | “Energy Conservation Program: Energy Conservation Standards . . .", 75 Federal Register 5 (8 January 2010), pp. 1123
ENERGY STAR Water Cooler | Miscellaneous | kWh = (ENERGYBASE - ENERGYEFF) x 365 |  | Efficient Water Cooler Energy Consumption (ENERGYEFF) | 0.69 | kWh/day | ENERGY STAR Certified Water Coolers Qualified Products List, Average of all models, Accessed 1/4/16
ENERGY STAR Water Cooler | Miscellaneous | kWh = (ENERGYBASE - ENERGYEFF) x 365 |  | Baseline Water Cooler Energy Consumption (ENERGYBASE) | 2.19 | kWh/day | Pennsylvania Statewide TRM, June 2016, Errata Update February 2017, Section 2.4.9, Table 2-94, Page 165
Engine Block Timer | Miscellaneous | delta_kWh = P_heater * T_heater * days * UF * SVGE |  | days heater will operate (days) | 90 | days/year | State of Minnesota Technical Reference Manual for Energy Conservation Improvements, Version 2.0, January 2017 - December 2019
Engine Block Timer | Miscellaneous | delta_kWh = P_heater * T_heater * days * UF * SVGE |  | Avg. power of engine block heater (p_heater) | 1 | kilowatt | State of Minnesota Technical Reference Manual for Energy Conservation Improvements, Version 2.0, January 2017 - December 2019
Engine Block Timer | Miscellaneous | delta_kWh = P_heater * T_heater * days * UF * SVGE |  | Estimated savings percentage from timer (SVGE) | 0.36 | % | http://e3tnw.org/ItemDetail.aspx?id=381
Engine Block Timer | Miscellaneous | delta_kWh = P_heater * T_heater * days * UF * SVGE |  | usage factor (UF) | 0.8 | usage factor | State of Minnesota Technical Reference Manual for Energy Conservation Improvements, Version 2.0, January 2017 - December 2019
Engine Block Timer | Miscellaneous | delta_kWh = P_heater * T_heater * days * UF * SVGE |  | time that heater will operate if uncontrolled (t_heater) | 10 | hours/day | State of Minnesota Technical Reference Manual for Energy Conservation Improvements, Version 2.0, January 2017 - December 2019
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Efficiency of the energy-efficient motor (n_ee) | 0.95 | 0 | Epact vs. NEMA Premium
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Efficiency of the baseline motor (n_base) | 0.891 | 0 | Epact vs. NEMA Premium
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Annual run hours of the motor (RHRS) | 2600 | Hours/Year | https://www.boma.org/research/Documents/Find%20a%20Resource/Elevator%20Modernization%20Case%20Study.pdf
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Load Factor - Ratio between the actual load and the rated load. (LF) | 0.75 | 0 | California Public Utility Commission. Database for Energy Efficiency Resources 2005.
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Rated horsepower of the baseline and energy efficient motor (HP) | 20 | HP | Nexant eQuest 2014; PA TRM, June 2016, Errata Update February 2017, Section 3.3.1, Table 3-57; PA TRM, June 2016, Errata Update February 2017, Section 3.3.1, Table 3-58
Regenerative Drive Elevator Motor | Miscellaneous | delta_kWh = 0.746 x HP x (LF/n_base - LF/n_ee) x RHRS |  | Conversion from hp to kW (Conversion from hp to kW) | 0.746 | kW/hp
Server Virtualization | Miscellaneous | ΔkWh = (kWbaseline - kWw virt)*8760 |  | Wattage at 12.5% load for 20 single application servers (kWbaseline) | 2.8 | kW | The Uniform Methods Project, Chapter 20: Data Center IT Efficiency Measures, September 2011-December 2014
Server Virtualization | Miscellaneous | ΔkWh = (kWbaseline - kWw virt)*8760 |  | Average power of the two virtual host servers (kWw virt) | 0.4 | kW | The Uniform Methods Project, Chapter 20: Data Center IT Efficiency Measures, September 2011-December 2014
Solar Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_solar |  | Estimated heat pump pool heater savings factor (pool_solar) | 0.86111 | % | Calculated using: https://www.riverpoolsandspas.com/blog/how-much-money-does-swimming-pool-heat-pumps-really-save
Solar Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_solar |  | Estimated electric pool heater consumption w/ cover (Pool_base) in FL Zone 2 | 11764.7059 | kWh/ year | https://www.energy.gov/energysaver/heat-pump-swimming-pool-heaters
Solar Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_solar |  | Estimated electric pool heater consumption w/ cover (Pool_base) in FL Zone 1 | 12647.0588 | kWh/ year | https://www.energy.gov/energysaver/heat-pump-swimming-pool-heaters
Heat Pump Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_ashp |  | Estimated heat pump pool heater savings factor (poolashpf) | 0.8 | % | https://www.energy.gov/energysaver/heat-pump-swimming-pool-heaters
Heat Pump Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_ashp |  | Estimated electric pool heater consumption w/ cover (Pool_base) in FL Zone 2 | 11764.7059 | kWh/ year | https://www.energy.gov/energysaver/heat-pump-swimming-pool-heaters
Heat Pump Pool Heater | Miscellaneous | delta_kWh = Pool_base x Pool_ashp |  | Estimated electric pool heater consumption w/ cover (Pool_base) in FL Zone 1 | 12647.0588 | kWh/ year | https://www.energy.gov/energysaver/heat-pump-swimming-pool-heaters
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump low speed daily operating hours (HOU_low) | 10 | hours/day | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Days of Pool Pump Operation (pooldays) | 365 | days per year | ENERGY STAR Pool Pump Calculator, Updated 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pool Volume (poolvol) | 22000 | gal | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump time to complete one turnover (turntime) | 12 | hours | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Single-Speed pump energy factor(EF_single) | 2.4 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump low speed energy factor(EF_low) | 7.26 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump high speed daily operating hours (HOU_high) | 2 | hours/day | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump high speed energy factor(EF_high) | 3.75 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Two Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pool turnovers per day (poolturn) | 1.5 | 0 | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Single-Speed pump energy factor(EF_single) | 2.4 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pool Volume (poolvol) | 22000 | gal | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Days of Pool Pump Operation (pooldays) | 365 | days per year | ENERGY STAR Pool Pump Calculator, Updated 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump low speed daily operating hours (HOU_low) | 11 | hours/day | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pool turnovers per day (poolturn) | 1.5 | 0 | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump time to complete one turnover (turntime) | 12 | hours | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump low speed energy factor(EF_low) | 7.26 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump high speed energy factor(EF_high) | 3.75 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Variable Speed Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [(1/EF_high x (HOU_high/turntime) + 1/EF_low x (HOU_low/turntime)) x poolvol x poolturn x pooldays/1,000] |  | Pump high speed daily operating hours (HOU_high) | 1 | hours/day | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Solar Capacity Factor (Solar_Cap) | 0.19 | %
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Single-Speed pump energy factor(EF_single) | 2.4 | gal/W*hour | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Days of Pool Pump Operation (pooldays) | 365 | days per year | ENERGY STAR Pool Pump Calculator, Updated 2013
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Pump time to complete one turnover (turntime) | 12 | hours | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Pool Volume (poolvol) | 22000 | gal | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
Solar Powered Pool Pump | Miscellaneous | kWh = [1/EF_single x poolvol x poolturn x pooldays/1,000] - [1/EF_single x poolvol x poolturn x pooldays/1,000 * Solar_Cap] |  | Pool turnovers per day (poolturn) | 1.5 |  | Arkansas TRM, Version 6.1, Section 3.7.12, based on ENERGY STAR Pool Pump Savings Calculator updated December 2013
VSD Controlled Compressor | Miscellaneous | delta_kWh= .445 x TONS x SVGE |  | Miscellaneous Energy Use Intensity (EUIMiscellaneous) | See Table Below | kWh/ft2/yr | Gulf LoadMap Commercial Results
VSD Controlled Compressor | Miscellaneous | delta_kWh= .445 x TONS x SVGE |  | Average Refrigeration Compressor Tonnage (TONS) | 20 | HP | Engineering Assumption
VSD Controlled Compressor | Miscellaneous | delta_kWh= .445 x TONS x SVGE |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
VSD Controlled Compressor | Miscellaneous | delta_kWh= .445 x TONS x SVGE |  | VSD Controlled Compressor Energy Savings (SVGE) | 1696 | kWh/Ton | Pennsylvania 2016 Statewide TRM, Section 3.5.8, Table 3-105
ENERGY STAR Imaging Equipment | Office Equipment | delta_kWh = (ENERGYBASE - ENERGYEFF) x 52.1 |  | ESImage_ENERGYEFF | 10 | kWh/week | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Using Standard format MFD Color unit with a speed of 30<s<=62 as proxy.
ENERGY STAR Imaging Equipment | Office Equipment | delta_kWh = (ENERGYBASE - ENERGYEFF) x 52.1 |  | ESImage_ENERGYBASE | 18 | kWh/week | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Using Standard format MFD Color unit with a speed of 30<s<=62 as proxy.
Energy Star PCs-Desktop | Office Equipment | delta_kWh = ENERGYBASE - ENERGYEFF |  | ESComp_(ENERGYEFF) | 161.4747 | kWh | ENERGY STAR Office Equipment Calculator, Downloaded 2018.
Energy Star PCs-Desktop | Office Equipment | delta_kWh = ENERGYBASE - ENERGYEFF |  | ESComp_(ENERGYBASE) | 284.9901 | kWh | ENERGY STAR Office Equipment Calculator, Downloaded 2018.
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(TON) | 2467.44 | Hours | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(TSLEEP) | 439.1936 | Hours | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(PIDLE,BASE) | 0.26098 | kW | 30% increase from ENERGY STAR Unit
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(PON,BASE) | 1.3772 | kW | 30% increase from ENERGY STAR Unit
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(PON,EFF) | 1.0594 | kW | ENERGY STAR Certified Servers Qualified Products List 2018, Power Supply Rated Output Typical or Single Configuration (W)
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(PIDLE,EFF) | 0.20075 | kW | ENERGY STAR Certified Servers Qualified Products List 2018, Idle Power Draw for Typical or Single Configuration (W)
Energy Star Servers | Office Equipment | delta_kWh = [(PON x TON) + (PIDLE x TIDLE)]BASE - [(PON x TON) + (PIDLE x TIDLE)]EFF |  | ServPow_Man_(TIDLE) | 5853.3952 | Hours | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Energy Star Uninterruptable Power Supply | Office Equipment | delta_kWh = ENERGYBASE x [1 - (EFFEFF - EFFBASE)] |  | UnintPow_(EFFBASE) | 0.9 | % | Schneider Electric White Paper #92: Comparison of Static and Rotary UPS, 2011
Energy Star Uninterruptable Power Supply | Office Equipment | delta_kWh = ENERGYBASE x [1 - (EFFEFF - EFFBASE)] |  | UnintPow_(ENERGYBASE) | 284.9901 | kWh | ENERGY STAR Office Equipment Calculator, Downloaded 2018.
Energy Star Uninterruptable Power Supply | Office Equipment | delta_kWh = ENERGYBASE x [1 - (EFFEFF - EFFBASE)] |  | UnintPow_(EFFEFF) | 0.91878 | % | ENERGY STAR Certified Uninterruptable Power Supplies Qualified Products List, Accessed April 2018, Average of all models available
Network PC Power Management | Office Equipment | delta_kWh = ( PCPowMan_kWhsavings * PCPowMan_Quant ) |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Network PC Power Management | Office Equipment | delta_kWh = ( PCPowMan_kWhsavings * PCPowMan_Quant ) |  | Computers Baseline EUI | See Table Below | kWh/ft2 | Estimated based on Gulf Loadmap Commercial Results
Network PC Power Management | Office Equipment | delta_kWh = ( PCPowMan_kWhsavings * PCPowMan_Quant ) |  | Assumed computer annual kwh baseline | 284.9702 | kWh | Estimated based on Energy Star Office Equipment Calculator, 2018
Network PC Power Management | Office Equipment | delta_kWh = ( PCPowMan_kWhsavings * PCPowMan_Quant ) |  | PCPowMan_kWhsavings | 161 | kWh | Illinois TRM, Version 6.0,Volume 2: Commercial and Industrial Measures for "unkown workstation type"
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | Computers Baseline EUI | See Table Below | kWh/ft2 | Estimated based on Gulf Loadmap Commercial Results
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | SmartStrip_(TimeCompOff) | 2467 | Hours | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | SmartStrip_(kWCompOff) | 0.96 | W | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | Assumed computer annual kwh baseline | 284.9702 | kWh | Estimated based on Energy Star Office Equipment Calculator, 2018
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | SmartStrip_(TimeCompSleep) | 439 | Hours | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Smart Strip Plug Outlet | Office Equipment | delta_kWh = SmartStrip_(kWCompIdle)*SmartStrip_(TimeCompIdle) |  | SmartStrip_(kWCompSleep) | 2.31 | W | ENERGY STAR Office Equipment Calculator, Downloaded 2018. Used Desktop Values
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | # of measures in a facility (ASQuant) | 1 | NA | Engineering Assumption
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | Residual Heat Fraction (Rh) | 0.65 |  | State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual, March 22, 2010.
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | Percent of time ASH with controls will be off annually (CHAoff) | 85 | % | State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual, March 22, 2010.
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | Coefficient of Performance (COPcool) | 2.5 |  | State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual, March 22, 2010.
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | Per door power consumption of ASHs without controls (kWcooler,base) | 0.109 | kW | State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual, March 22, 2010.
Anti-Sweat Controls | Refrigeration | delta_kWh= kWcooler,base x (8760 x CHAoff) x (1 + Rh / COPcool)*ASQuant |  | Hours per year | 8760 | hours
Automatic Door Closer for Walk-in Coolers and Freezers | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) x TIMEUNINTENTIONAL |  | Estimated Unintentional Refrigerated Case Door Open Time (TIMEUNINTENTIONAL) | 0.25 | % | Regional Technical Forum, Commercial: Grocery - Autoclosers V1.2
Automatic Door Closer for Walk-in Coolers and Freezers | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) x TIMEUNINTENTIONAL |  | Efficient Medium-Temp Refrigerated Case Energy Consumption (ENERGYEFF) | 14.6111 | kWh/day | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Automatic Door Closer for Walk-in Coolers and Freezers | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) x TIMEUNINTENTIONAL |  | Baseline Medium-Temp Refrigerated Case Energy Consumption (ENERGYBASE) | 15.0833 | kWh/day | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Automatic Door Closer for Walk-in Coolers and Freezers | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) x TIMEUNINTENTIONAL |  | Estimated Refrigerated Case Door Open Time (TIMEDOOR) | 0.093 | % | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Demand Defrost | Refrigeration | delta_kWh = EUICENTRAL AC x AREA x SVG |  | Demand Defrost Energy Savings Factor (SVGE) | 0.3 | % | Efficiency Vermont TRM No. 2014-87, Measure Number I-E-15-a
Demand Defrost | Refrigeration | delta_kWh = EUICENTRAL AC x AREA x SVG |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Demand Defrost | Refrigeration | delta_kWh = EUICENTRAL AC x AREA x SVG |  | Refrigeration Energy Use Intensity (EUIRefrigeration) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
High R-Value Glass Doors | Refrigeration | delta_kWh = ENERGYBASE - ENERGYEFF |  | Baseline Display Case Door Energy Consumption (ENERGYBASE) | 916.6667 | kWh/door | Market Research of vendor literature (www.anthonyintl.com)
High R-Value Glass Doors | Refrigeration | delta_kWh = ENERGYBASE - ENERGYEFF |  | Efficient Display Case Door Energy Consumption (ENERGYEFF) | 266.6667 | kWh/door | Market Research of vendor literature (www.anthonyintl.com)
Energy Star Commercial Glass Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Efficient Glass Door Freezer Energy Consumption (ENERGYEFF) | 17.618 | kWh/day | ENERGY STAR Certified Commercial Refrigerators and Freezers Qualified Product List, Average of all Glass Door Freezer Models within 25% of volume., Accessed 1/8/16
Energy Star Commercial Glass Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Baseline Glass Door Freezer Energy Consumption (ENERGYBASE) | 29.6453 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-91
Energy Star Commercial Glass Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Energy Star Commercial Glass Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Energy Star Commercial Glass Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Baseline Glass Door Refrigerator Energy Consumption (ENERGYBASE) | 6.6745 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-90
Energy Star Commercial Glass Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Efficient Glass Door Refrigerator Energy Consumption (ENERGYEFF) | 4.1461 | kWh/day | ENERGY STAR Certified Commercial Refrigerators and Freezers Qualified Product List, Average of all Glass Door Freezer Models within 10% of volume., Accessed 1/8/16
Energy Star Commercial Solid Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Energy Star Commercial Solid Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Baseline Solid Door Freezer Energy Consumption (ENERGYBASE) | 16.4799 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-91
Energy Star Commercial Solid Door Freezer | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Efficient Solid Door Freezer Energy Consumption (ENERGYEFF) | 9.54 | kWh/day | ENERGY STAR Certified Commercial Refrigerators and Freezers Qualified Product List, Average of all Glass Door Freezer Models within 10% of volume., Accessed 1/8/16
Energy Star Commercial Solid Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Baseline Solid Door Refrigerator Energy Consumption (ENERGYBASE) | 4.6315 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-90
Energy Star Commercial Solid Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Efficient Solid Door Refrigerator Energy Consumption (ENERGYEFF) | 2.3029 | kWh/day | ENERGY STAR Certified Commercial Refrigerators and Freezers Qualified Product List, Average of all Glass Door Freezer Models within 10% of volume., Accessed 1/8/16
Energy Star Commercial Solid Door Refrigerator | Refrigeration | delta_kWh = (ENERGYBASE - ENERGYEFF) x DAYS |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | Baseline ice machine energy usage per 100 lbs. of ice (kWhbase) | 5.637 | kWh/100lbs | Based on maximum energy use of each continuous type automatic commercial ice maker with capacities between 50 and 4,000 pounds per 24-hour period manufactured on or after January 28, 2018, shall meet the following standard levels. Calculations
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | Ice harvest rate per 24 hrs (H) | 650 | lbs/day | Engineering Assumption
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | High-efficiency ice machine energy usage per 100 lbs. of ice (kWhee) | 4.995 | kWh/100lbs | Commercial Ice Maker Key Product Criteria Version 3.0 https://www.energystar.gov/products/commercial_food_service_equipment/commercial_ice_makers/key_product_criteria
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | Conversion to obtain energy per pound of ice (Conversion to obtain energy per pound of ice) | 100 | lbs/100lbs
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | # of measures in a facility (IMQuant) | 1 | NA | Engineering Assumption
Energy Star Ice Maker | Refrigeration | kWh = (kWhbase - kWhee)/100 x H x 365 x DC x IMQuant |  | Duty cycle of ice maker - percentage of time machine produces ice (DC) | 57 | % | This value from study in Vermont, Wisconsin, and New York. State of OH EE TRM cites a default duty cycle of 40% as a conservative value. Other studies range as high as 75%.
Energy Star Refrigerator | Refrigeration | delta_kWh = UEC_base - UEC_efficient |  | Refrigerator Unit Energy Consumption ENERGY STAR (refuecestar) | 473.63 | Annual kWh | PA TRM 2014 and Evaluation of Georgia Power Company's 2014 Residential DSM Programs. Nexant, July 2015.
Energy Star Refrigerator | Refrigeration | delta_kWh = UEC_base - UEC_efficient |  | Refrigerator Unit Energy Consumption Baseline (refuecbase) | 607.13 | Annual kWh | PA TRM 2014 and Evaluation of Georgia Power Company's 2014 Residential DSM Programs. Nexant, July 2015.
Energy Star Vending Machine | Refrigeration | delta_kWh = ENERGYBASE x DAYS x SVGE x VMQuant |  | # of measures in a facility (VMQuant) | 1
Energy Star Vending Machine | Refrigeration | delta_kWh = ENERGYBASE x DAYS x SVGE x VMQuant |  | Baseline Vending Machine Electric Demand (ENERGYBASE) | 4.001 | kWh/day | Based on energy star Class A (fully cooled) vending machine kWh/day based on equation Class A – New and Rebuilt Machines: 0.0523V + 2.432 where "V" is the volume in cubic feet (estimated at 30 cuft here) https://www.energystar.gov/products/othe
Energy Star Vending Machine | Refrigeration | delta_kWh = ENERGYBASE x DAYS x SVGE x VMQuant |  | Vending Machine Operating Days (DAYS) | 365 | Days | Engineering Assumption
Energy Star Vending Machine | Refrigeration | delta_kWh = ENERGYBASE x DAYS x SVGE x VMQuant |  | Vending Machine Controls Energy Savings Factor (SVGE) | 0.36 | % | Regional Technical Forum, Grocery - Vending Machine Controller V1.0
Floating Head Pressure Controls | Refrigeration | delta_kWh = HP x SVGE |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Floating Head Pressure Controls | Refrigeration | delta_kWh = HP x SVGE |  | Floating Head Pressure Controller on Refrigerator Energy Savings Factor (SVGE) | 504.7143 | kWh/HP | Pennsylvania 2016 Statewide TRM, Section 3.5.5, Table 3-100
Floating Head Pressure Controls | Refrigeration | delta_kWh = HP x SVGE |  | Compressor Horsepower (HP) | 5 | HP | Measure Definition
Floating Head Pressure Controls | Refrigeration | delta_kWh = HP x SVGE |  | Refrigeration Energy Use Intensity (EUIRefrigeration) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Freezer-Cooler Replacement Gaskets | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) |  | Estimated Refrigerated Case Door Open Time (TIMEDOOR) | 0.093 | % | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Freezer-Cooler Replacement Gaskets | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) |  | Baseline Medium-Temp Refrigerated Case Energy Consumption (ENERGYBASE) | 15.0833 | kWh/day | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Freezer-Cooler Replacement Gaskets | Refrigeration | delta_kWh= (ENERGYBASE - ENERGYEFF) x 365 x (1 - TIMEDOOR) |  | Efficient Medium-Temp Refrigerated Case Energy Consumption (ENERGYEFF) | 14.6111 | kWh/day | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
High Efficiency Refrigeration Compressor | Refrigeration | delta_kWh = ENERGYBASE - ENERGYEFF |  | Energy Consumption of Efficient Discus Refrigeration Compressor (ENERGYEFF) | 1822 | kWh | 2014 IESO Measures and Assumptions Document
High Efficiency Refrigeration Compressor | Refrigeration | delta_kWh = ENERGYBASE - ENERGYEFF |  | Baseline Refrigeration Compressor Energy Consumption (ENERGYBASE) | 1957.5 | kWh | Regional Technical Forum, Commercial: Grocery - AntiSweatHeaterControls V2.1
High Efficiency Refrigeration Compressor | Refrigeration | delta_kWh = ENERGYBASE - ENERGYEFF |  | Existing Refrigeration Compressor Energy Consumption (ENERGYBASE) | 2153.25 | kWh | Assumed 10% less efficient than baseline
Night Covers for Display Cases | Refrigeration | delta_kWh = (ENERGYBASE x DAYS) x SVGE |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Night Covers for Display Cases | Refrigeration | delta_kWh = (ENERGYBASE x DAYS) x SVGE |  | Baseline Medium-Temp Refrigerated Case Energy Consumption (ENERGYBASE) | 15.0833 | kWh/day | Regional Technical Forum, Commercial: Grocery - Door Gasket Replacement V1.4
Night Covers for Display Cases | Refrigeration | delta_kWh = (ENERGYBASE x DAYS) x SVGE |  | Vertical Night Covers Energy Savings Factor (SVGE) | 0.018765 | % | Regional Technical Forum, Commercial: Grocery - Night Covers V1.0
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Number of evaporator fans (nFans) | 2 |  | Engineering Assumption
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Connected load kW of the circulating fan (kWCirc) | 0.035 | kW | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Number of annual hours that economizer operates (Hours) | 1968 | Hours | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Condensing unit savings, per hp (kWhCond) | 1138.3333 | kWh/HP | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers Average of condensing unit types
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Duty cycle of the compressor (DCComp) | 0.5 |  | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Duty cycle of the economizer fan on operational days (DEEcon) | 0.63 |  | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | # of measures in a facility (OAEQuant) | 1 | NA | Engineering Assumption
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Bonus factor for reduced cooling load from evaporator fan (BF) | 1.2857 |  | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Space Cooling Energy Use Intensity (EUISpace Cooling) | See Table Below | kWh/ft2/yr | Gulf UEC data
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Connected load kW of the economizer fan (kWEcon) | 0.227 | kW | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Horsepower of Compressor (HP) | 5 | hp | Engineering Assumption
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Connected load kW of each evaporator fan (kWEvap) | 0.123 | kW | IL-TRM_Effective_010118_v6.0_Vol_2_C_and_I_020817_Final 4.6.8 Refrigeration Economizers
Outside Air Economizer for Coolers | Refrigeration | delta_kWh = [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon* Hours] *OAEQuant |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Reach-In Case Hours of Use (HOU) | 8760 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Duty Cycle of Evaporator Fan Motor for Cooler (DC) | 1 | % | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Permanent Split Capacitor Fan Motor Electric Demand (kWBASE) | 0.048 | kW | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-91
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Electronically Commutated Fan Motor Electric Demand (kWEFF) | 0.03 | kW | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-91
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Reach-In Cooler Compressor Coefficient of Performance (COP) | 2.5 |  | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Reach-In Case Fan Load Factor (LF) | 0.9 |  | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Reach-In) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Compressor Degradation Factor (DG) | 0.98 |  | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Walk-In Freezer Compressor Coefficient of Performance (COP) | 1.3 |  | Pennsylvania 2016 Statewide TRM, Section 3.5.3, Table 3-93
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Permanent Split Capacitor Fan Motor Electric Demand (kWBASE) | 0.048 | kW | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-91
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Walk-In Case Hours of Use (HOU) | 8273 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.5.3, Table 3-93
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Walk-In Case Fan Load Factor (LF) | 1 | % | Pennsylvania 2016 Statewide TRM, Section 3.5.3, Table 3-93
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Duty Cycle of Evaporator Fan Motor for Freezer (DC) | 0.944 | % | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Compressor Degradation Factor (DG) | 0.98 |  | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-89
PSC to ECM Evaporator Fan Motor (Walk-In, Refrigerator) | Refrigeration | delta_kWh = (kWBASE - kWEFF) x LF x DC x [1 + (1 / DG x COP)] x HOU |  | Electronically Commutated Fan Motor Electric Demand (kWEFF) | 0.03 | kW | Pennsylvania 2016 Statewide TRM, Section 3.5.2, Table 3-91
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Refrigerated Case Lighting Interactive Factor (IF) | 0.465 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.7, Table 3-22 (Average of Freezer and Cooler)
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 28.16 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Refrigerated Case Lighting Hours of Use (HOU) | 6205 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.1.7, Table 3-22
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 28.7247 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Baseline Glass Door Refrigerator Energy Consumption (ENERGYBASE) | 6.67 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-90
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Efficient Linear Fluorescent Lamp/Fixture Type | GE Immersion 60" LED, Average |  | Measure Definition
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Quantity of Lamps per Linear Fluorescent Fixture | 1 |  | Measure Definition
Refrigerated Display Case LED Lighting | Refrigeration | delta_kWh = (kWBASE - kWEFF) / 1000 x HOU x (1 + IF) |  | Power of Efficient Refrigerated Case LED (kWBASE) | 10.45 | W | GE Immersion LED Refrigerated Display Lighting Technical Guide, Average of Center and End Units
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Power of Efficient Refrigerated Case LED (kWBASE) | 10.45 | W | GE Immersion LED Refrigerated Display Lighting Technical Guide, Average of Center and End Units
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Power of Lumen-Equivalent Baseline Linear Fluorescent Fixture (kWBASE) | 28.16 | W | Osram Sylvania 's 2014-2015 Lamp and Ballast Catalog, and Pennsylvania 2016 Statewide TRM, Appendix C
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Refrigerated Case Lighting Interactive Factor (IF) | 0.465 |  | Pennsylvania 2016 Statewide TRM, Section 3.1.7, Table 3-22 (Average of Freezer and Cooler)
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Baseline Glass Door Refrigerator Energy Consumption (ENERGYBASE) | 6.67 | kWh/day | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-90
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Power of Existing Linear Fluorescent Fixture (kWBASE) | 28.7247 | W | Pennsylvania 2016 Statewide TRM, Appendix C & Pennsylvania Statewide Act 129 2014 Commercial and Residential Light Metering Study Report
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Occupancy Sensor Savings Factor (SVGEE) | 0.24 | % | Pennsylvania 2016 Statewide TRM, Section 3.1.1, Table 3-4
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Quantity of Lamps per Linear Fluorescent Fixture | 1 |  | Measure Definition
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Efficient Linear Fluorescent Lamp/Fixture Type | GE Immersion 60" LED, Average |  | Measure Definition
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Refrigerator/Freezer Operating Days (DAYS) | 365 | Days | Pennsylvania 2016 Statewide TRM, Section 3.5.1, Table 3-89
Refrigerated Display Case Lighting Controls | Refrigeration | delta_kWh = kWBASE / 1000 x HOU x (1 + IF) x SVGEE |  | Refrigerated Case Lighting Hours of Use (HOU) | 6205 | Hours | Pennsylvania 2016 Statewide TRM, Section 3.1.7, Table 3-22
Strip Curtains for Walk-ins | Refrigeration | delta_kWh = delta_kWh x A |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Strip Curtains for Walk-ins | Refrigeration | delta_kWh = delta_kWh x A |  | Avg. Walk-in Freezer Annual Consumption | 19854.7304 | kWh | http://www.uscooler.com/refrigeration-sizing-estimate/
Strip Curtains for Walk-ins | Refrigeration | delta_kWh = delta_kWh x A |  | Strip Curtains Deemed Savings, per sqft of doorway (kWh) | 20 | kWh/sqft | IL TRM 2017 Table 4.6.7-1 Using Convenience Store cooler with no existing curtains
Strip Curtains for Walk-ins | Refrigeration | delta_kWh = delta_kWh x A |  | Refrigeration Energy Use Intensity (EUIRefrigeration) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Strip Curtains for Walk-ins | Refrigeration | delta_kWh = delta_kWh x A |  | Avg Walk-in Refrigerator/Freezer Doorway Area (A) | 21 | sq. ft | PA TRM 2015
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | Standard Motor Load Factor (LF) | 0.75 |  | Minnesota 2016 Statewide TRM V1.3, C/I Motors V2.0
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | 10 HP, Existing ODP Motor Efficiency, Assumed 4-Poles (EFFBASE) | 0.895 | % | NEMA MG-1, Table 12-11 (Sourced from Marathon Electric, http://www.marathonelectric.com/docs/MG1EffCharts.pdf)
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | 10 HP, Efficient ODP Motor Efficiency, Assumed 4-Poles (EFFEFF) | 0.927 | % | Minnesota 2016 Statewide TRM V1.3, Appendix C - C/I Motor Tables
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | 10 HP, Baseline ODP Motor Efficiency, Assumed 4-Poles (EFFBASE) | 0.917 | % | NEMA MG-1, Table 12-11 (Sourced from Marathon Electric, http://www.marathonelectric.com/docs/MG1EffCharts.pdf)
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | 10 HP Motor Annual Run Hours (RHRS) | 3391 | Hours | Minnesota 2016 Statewide TRM V1.3, C/I Motors, Table 1
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | Motor Configuration | ODP |  | Measure Definition
10HP Open Drip-Proof(ODP) Motor | Ventilation and Circulation | delta_kWh = 0.746 x HP x [(LF/EFFBASE) - (LF/EFFEFF)] x RHRS |  | Rated Motor Horsepower (HP) | 10 | HP | Measure Definition
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Unit motor horsepower of a typical ventilation fan | 1 | Hp | Engineering Assumption based on Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Ventilation fan annual operating hours, typically 8766 | 8766 | hr | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Annual reduction in operating hours | 0.33 | % | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Conversion Factor, C1 | 62 | Kw/hp | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Motor Load Factor | 0.7 |  | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Motor efficiency for typical motor | 0.91 | % | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
CO Sensors for Parking Garage Exhaust | Ventilation and Circulation | delta_kWh = (HP x LF x UF x C1 x t x SF) / ɳmotor |  | Motor Usage Factor | 1 |  | Minnesota TRM version 2.0, Parking Garage Exhaust Fan CO Control and Heating
Demand Controlled Ventilation | Ventilation and Circulation | delta_kWh = AREA/1000 x SVG |  | Ventilation and Circulation Energy Use Intensity (EUIVentilation and Circulation) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Demand Controlled Ventilation | Ventilation and Circulation | delta_kWh = AREA/1000 x SVG |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Demand Controlled Ventilation | Ventilation and Circulation | delta_kWh = AREA/1000 x SVG |  | Demand Controlled Ventilation Energy Savings Factor (SVGE) | 451.0625 | kWh/1000ft2 | Illinois 2015 Statewide Technical Reference Manual, Section 4.4.19
High Speed Fans | Ventilation and Circulation | delta_kWh = (Fan_kW_Base-Fan_kW_EE) * Hours |  | Circulation baseline efficiency average kW rating (Fan_kW_Base) | 0.6217 |  | Wisconsin Focus on Energy 2017 Technical Reference Manual.
High Speed Fans | Ventilation and Circulation | delta_kWh = (Fan_kW_Base-Fan_kW_EE) * Hours |  | Circulation energy-efficient fan average kW rating (Fan_kW_EE) | 0.5534 |  | Wisconsin Focus on Energy 2017 Technical Reference Manual.
High Speed Fans | Ventilation and Circulation | delta_kWh = (Fan_kW_Base-Fan_kW_EE) * Hours |  | Annual Hours of Operation (Hours) | 7446 | hrs | Wisconsin Focus on Energy 2017 Technical Reference Manual.
VAV System | Ventilation and Circulation | delta_kWh = SVGE x AREA |  | Ventilation and Circulation Energy Use Intensity (EUIVentilation and Circulation) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
VAV System | Ventilation and Circulation | delta_kWh = SVGE x AREA |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
VAV System | Ventilation and Circulation | delta_kWh = SVGE x AREA |  | Commercial VAV System Energy Savings Factor (SVGE) | 3.62 | kWh/ft2 | "Chapter 8: Air Distribution Systems". Energy Star Building Manual. April, 2008. Table 8.1
Retro-Commissioning | Whole Building | delta_kWh = EUITotal x AREA x SVGE |  | Average Premise Area (AREA) | See Table Below | Square Feet | End-Use Study
Retro-Commissioning | Whole Building | delta_kWh = EUITotal x AREA x SVGE |  | All Energy Use Intensity (EUIAll) | See Table Below | kWh/ft2/yr | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey
Retro-Commissioning | Whole Building | delta_kWh = EUITotal x AREA x SVGE |  | Retrocommissioning Energy Savings Factor (SVGE) | 0.16 | % | Pennsylvania Public Utility Commission, Energy Efficiency Potential Study for Pennsylvania Final Report, 2015, Appendix E
Thermal Energy Storage | HVAC | delta_kWh = SVGE |  | Thermal Energy Storage Energy Savings Value (SVGE) | -72164 | kWh | FEECA Utility Program Participation Data

## "See Table Below"
General Building Characteristics (FL Zone 1 & 2)
Segment | Average Premise Area (AREA) | Average Premise Number of Floors (NFLOORS) | Lighting HOU
Assembly | 19267 | 1.5179 | 2876
College and University | 75933 | 2.9222 | 4408
Grocery | 4712 | 1.2623 | 5544
Healthcare | 20121 | 1.502 | 5028
Hospitals | 209655 | 8.096 | 6802
Institutional | 20630 | 4.9703 | 3299
Lodging/Hospitality | 33805 | 6.1268 | 3754
Miscellaneous | 30667 | 1.4768 | 4408
Offices | 16065 | 5.6169 | 3253
Restaurants | 5080 | 1.3205 | 3357
Retail | 11444 | 1.2995 | 4984
Schools K-12 | 52061 | 1.3501 | 2379
Warehouse | 16064 | 1.152 | 3824
Sources: | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey, Calculated based on Total Floorspace by Principal Building Activity by Region (South Atlantic Census Division) |  | Indiana TRM Version 2.1, July 15, 2015
Energy Use Intensity (EUI) (FL Zone 1 & 2)
Segment | All | Interior Lighting | Exterior Lighting | Office Equipment | Cooking | Refrigeration | Space Heating | Space Cooling | Ventilation and Circulation | Domestic Hot Water | Miscellaneous
Assembly | 8.64 | 1.9 | 0.2 | 2.1 | 0.2 | 0.4 | 0.4 | 2.1 | 0.5 | 0.2 | 0.5
College and University | 10.98 | 2.9 | 0.4 | 1.1 | 0.4 | 0.7 | 0.6 | 3.2 | 0.7 | 0.3 | 0.8
Grocery | 71.31 | 18.7 | 2.3 | 7 | 2.4 | 4.3 | 3.8 | 20.7 | 4.8 | 2.1 | 5.2
Healthcare | 29.15 | 7.6 | 1 | 2.8 | 1 | 1.7 | 1.6 | 8.5 | 2 | 0.9 | 2.1
Hospitals | 29.15 | 7.6 | 1 | 2.8 | 1 | 1.7 | 1.6 | 8.5 | 2 | 0.9 | 2.1
Institutional | 32.86 | 8.6 | 1.1 | 3.2 | 1.1 | 2 | 1.8 | 9.6 | 2.2 | 1 | 2.4
Lodging/Hospitality | 16.45 | 4.3 | 0.5 | 1.6 | 0.5 | 1 | 0.9 | 4.8 | 1.1 | 0.5 | 1.2
Miscellaneous | 210.76 | 55.3 | 6.9 | 20.6 | 7 | 12.6 | 11.4 | 61.3 | 14.1 | 6.3 | 15.4
Offices | 30.07 | 7.9 | 1 | 2.9 | 1 | 1.8 | 1.6 | 8.7 | 2 | 0.9 | 2.2
Restaurants | 68.92 | 18.1 | 2.2 | 6.7 | 2.3 | 4.1 | 3.7 | 20 | 4.6 | 2.1 | 5
Retail | 13.36 | 3.5 | 0.4 | 1.3 | 0.4 | 0.8 | 0.7 | 3.9 | 0.9 | 0.4 | 1
Schools K-12 | 10.98 | 2.9 | 0.4 | 1.1 | 0.4 | 0.7 | 0.6 | 3.2 | 0.7 | 0.3 | 0.8
Warehouse | 3.53 | 0.9 | 0.1 | 0.3 | 0.1 | 0.2 | 0.2 | 1 | 0.2 | 0.1 | 0.3
Sources: | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results | Gulf LoadMap Commercial Results
FL Zone 1 (FPL-specific) HVAC Parameter
Segment | FELHCOOL | FEHLHEAT | CAPY | EER
Assembly | 1841.5052 | 0 | 62400 | 9.2
College and University | 2042.9859 | 0 | 30000 | 8.7
Grocery | 1017.2661 | 0 | 62400 | 9.2
Healthcare | 4007.0702 | 30.4769 | 85200 | 11.3
Hospitals | 3795.7268 | 0 | 85200 | 11.3
Institutional | 994.7228 | 0 | 58800 | 10.6
Lodging/Hospitality | 3041.9355 | 20.5253 | 62400 | 9.2
Miscellaneous | 1028.5377 | 10.7291 | 43200 | 9.8
Offices | 2072.5739 | 11.3511 | 67200 | 10.6
Restaurants | 2984.1683 | 71.6829 | 48000 | 9.3
Retail | 2338.8666 | 44.9379 | 74400 | 8.3
Schools K-12 | 2033.1232 | 41.3615 | 30000 | 8.7
Warehouse | 446.639 | 0 | 42000 | 7
Sources: | Texas PUC TRM, v5.0, Volume 3, adjusted based on ratio of CDD from Houston and FPL territory | Texas PUC TRM, v5.0, Volume 3, adjusted based on ratio of HDD from Houston and FPL territory | Pennsylvania Statewide Act 129 2014 Baseline and End-Use Study Report | Pennsylvania Statewide Act 129 2014 Baseline and End-Use Study Report
FL Zone 2 HVAC Parameter | *NOTE - Will be customized for each Zone 2 utility based on appropriate weather stations
Segment | FELHCOOL | FEHLHEAT | CAPY | EER
Assembly | 1464.0452 | 0 | 62400 | 9.2
College and University | 1624.2277 | 0 | 30000 | 8.7
Grocery | 808.7534 | 0 | 62400 | 9.2
Healthcare | 3185.7265 | 98.8059 | 85200 | 11.3
Hospitals | 3017.703 | 0 | 85200 | 11.3
Institutional | 790.8308 | 0 | 58800 | 10.6
Lodging/Hospitality | 2418.419 | 66.5427 | 62400 | 9.2
Miscellaneous | 817.7146 | 34.7837 | 43200 | 9.8
Offices | 1647.751 | 36.8002 | 67200 | 10.6
Restaurants | 2372.4925 | 232.3955 | 48000 | 9.3
Retail | 1859.4606 | 145.6883 | 74400 | 8.3
Schools K-12 | 1616.3866 | 134.0937 | 30000 | 8.7
Warehouse | 355.0898 | 0 | 42000 | 7
Sources: | Texas PUC TRM, v5.0, Volume 3, adjusted based on ratio of CDD from Houston and FL Climate Zone 2 | Texas PUC TRM, v5.0, Volume 3, adjusted based on ratio of HDD from Houston and FL Climate Zone 2 | Pennsylvania Statewide Act 129 2014 Baseline and End-Use Study Report | Pennsylvania Statewide Act 129 2014 Baseline and End-Use Study Report
Annual Gallons of Hot Water Use (HW) (FL Zone 1 & 2)
Segment | HW
Assembly | 54750
College and University | 1259250
Grocery | 109500
Healthcare | 73000
Hospitals | 2208250
Institutional | 4380000
Lodging/Hospitality | 525600
Miscellaneous | 3285000
Offices | 456250
Restaurants | 182500
Retail | 325215
Schools K-12 | 22813
Warehouse | 109500
Source | Indiana TRM Version 2.1, July 15, 2015
FL Zone 1 Lighting Parameter - Code Required Controls Saving Factor (SVGBASE)
Segment | SVGBASE
Assembly | 0
College and University | 0
Grocery | 0
Healthcare | 0
Hospitals | 0
Institutional | 0
Lodging/Hospitality | 0
Miscellaneous | 0
Offices | 0
Restaurants | 0
Retail | 0
Schools K-12 | 0
Warehouse | 0
Source
FL Zone 2 Lighting Parameter - Code Required Controls Saving Factor (SVGBASE)
Segment | SVGBASE
Assembly | 0
College and University | 0
Grocery | 0
Healthcare | 0
Hospitals | 0
Institutional | 0
Lodging/Hospitality | 0
Miscellaneous | 0
Offices | 0
Restaurants | 0
Retail | 0
Schools K-12 | 0
Warehouse | 0
Source
Average Number of Showerheads (NOSHOWER) (FL Zone 1 &2)
Segment | NOSHOWER
Assembly | 1
College and University | 8
Grocery | 1
Healthcare | 1
Hospitals | 1
Institutional | 8
Lodging/Hospitality | 1
Miscellaneous | 13
Offices | 1
Restaurants | 1
Retail | 1
Schools K-12 | 1
Warehouse | 1
Sources: | based on PA showerheads workbook, F:\Projects\PA SWE Phase II\PA Phase II Potential Study\Task 4 - Measure Research\Measure Research\MEASURE WORKBOOKS\Commercial\Water Heating\Low-Flow Showerheads.xlsx
Computers Baseline EUI (FL Zone 1&2)
Segment | Computers Baseline EUI
Assembly | 0.24
College and University | 0.16
Grocery | 1.27
Healthcare | 0.42
Hospitals | 0.35
Institutional | 0.37
Lodging/Hospitality | 0.2
Miscellaneous | 3.37
Offices | 0.36
Restaurants | 1.11
Retail | 0.22
Schools K-12 | 0.16
Warehouse | 0.04
Sources: | Estimated based on Gulf Loadmap Commercial Results
Average Premise Number of Floors (NFLOORS) (FL Zone 1 &2)
Segment | NFLOORS
Assembly | 1.52
College and University | 2.92
Grocery | 1.26
Healthcare | 1.5
Hospitals | 8.1
Institutional | 4.97
Lodging/Hospitality | 6.13
Miscellaneous | 1.48
Offices | 5.62
Restaurants | 1.32
Retail | 1.3
Schools K-12 | 1.35
Warehouse | 1.15
Sources: | US Energy Information Administration, 2012 Commercial Buildings Energy Consumption Survey, Calculated based on Number of Floors by Principal Building Activity by Region (South Atlantic Census Division)
FL Zone 1 Heating Degree Days (HDD)
FL Zone 1 Cooling Degree Days (CDD)
Segment | HDD | CDD
Assembly | 203.27 | 4307.53
College and University | 203.27 | 4307.53
Grocery | 203.27 | 4307.53
Healthcare | 203.27 | 4307.53
Hospitals | 203.27 | 4307.53
Institutional | 203.27 | 4307.53
Lodging/Hospitality | 203.27 | 4307.53
Miscellaneous | 203.27 | 4307.53
Offices | 203.27 | 4307.53
Restaurants | 203.27 | 4307.53
Retail | 203.27 | 4307.53
Schools K-12 | 203.27 | 4307.53
Warehouse | 203.27 | 4307.53
Sources: | Adjusted number derived from National Weather Service Forecast Office based on sales distribution of FPL | Adjusted number derived from National Weather Service Forecast Office based on sales distribution of FPL
FL Zone 2 Heating Degree Days (HDD)
FL Zone 2 Cooling Degree Days (CDD) | *NOTE - Will be customized for each Zone 2 utility based on appropriate weather stations
Segment | HDD | CDD
Assembly | 528 | 3517
College and University | 528 | 3517
Grocery | 528 | 3517
Healthcare | 528 | 3517
Hospitals | 528 | 3517
Institutional | 528 | 3517
Lodging/Hospitality | 528 | 3517
Miscellaneous | 528 | 3517
Offices | 528 | 3517
Restaurants | 528 | 3517
Retail | 528 | 3517
Schools K-12 | 528 | 3517
Warehouse | 528 | 3517
Sources: | Adjusted number derived from National Weather Service Forecast Office based on sales distribution of FPL | Adjusted number derived from National Weather Service Forecast Office based on sales distribution of FPL
Baseline Commercial Fenestration, U-Value (UBASE) (FL Zone 1 & 2)
Existing Commercial Below-Grade Wall Insulation, R-Value (RBASE) (FL Zone 1 & 2)
Segment | UBASE | RBASE
Assembly | 0.5 | 2
College and University | 0.5 | 2
Grocery | 0.5 | 2
Healthcare | 0.5 | 2
Hospitals | 0.5 | 2
Institutional | 0.5 | 2
Lodging/Hospitality | 0.5 | 2
Miscellaneous | 0.5 | 2
Offices | 0.5 | 2
Restaurants | 0.5 | 2
Retail | 0.5 | 2
Schools K-12 | 0.5 | 2
Warehouse | 0.5 | 2
Sources: | IECC 2012 | End-Use Study
Energy Recovery Ventilation Savings Factors
Segment | Zone 2 | FPL (Zone 1/2)
Assembly | 0.1824 | 0.19367
College and University | 0.1024 | 0.122
Grocery | 0.09935 | 0.12
Healthcare | 0.09935 | 0.12
Hospitals | 0.09935 | 0.12
Institutional | 0.09935 | 0.12
Lodging/Hospitality | 0.09935 | 0.12
Miscellaneous | 0.09935 | 0.12
Offices | 0.0612 | 0.071667
Restaurants | 0.109 | 0.13833
Retail | 0.1248 | 0.148
Schools K-12 | 0.1024 | 0.122
Warehouse | 0.09935 | 0.12
Sources: | FPL Technical Primer - Energy Recovery Ventilation | FPL Technical Primer - Energy Recovery Ventilation