## RMargin_Calculations_MP
Winter | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Winter |  | Renewables |  |  | Peaker and Suwannee Retirements
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year | (MW) | SUWBIOM | SOLAR_ST | BIOMASS |  |  | Winter | Summer
2011 | 12876.22 | 9577.423 |  | 1383.3124 | 34.44% | 34.4435 | -1.81e-05% | CR4 Der / Miller UPS | Vandolah Reliant / Scherer / Franklin / CR3 Uprate | -434 | 571.58 |  |  | -20 | [5 empty] | -414 | 571.58 |  |  |  |  | 2011 | 2011 | 0 | 0 | 0 | Avon Park | 1 | 34 | 24 | May | 2021
2012 | 12969.472 | 9640.423 | 63 | 1400.9644 | 34.53% | 34.5322 | -1.941e-06% | TECO | Vandolah Reliant | -70 | 163.252 | [7 empty] | 3.672 | -70 | 159.58 |  |  |  |  | 2012 | 2012 | 0 | 0 | 0 | Avon Park | 2 | 35 | 24 | May | 2021
2013 | 13317.4704 | 9716.423 | 76 | 1657.7628 | 37.06% | 37.0615 | -1.848e-05% | Vandolah Reliant | Vandolah NSG | -319.16 | 667.1584 | [8 empty] | -319.16 | 667.1584 |  |  |  |  | 2013 | 2013 | 0 | 0 | 0 | Higgins | 1 | 25 | 25 | May | 2021
2014 | 13226.8224 | 9730.423 | 14 | 1550.3148 | 35.93% | 35.9327 | -1.425e-05% | Lake Cogen / LFC / El Dorado | CR3 Uprate | -241.2 | 150.552 | [7 empty] | 150.552 |  |  |  |  | -241.2 |  | 2014 | 2014 | 0 | 0 | 40 | Higgins | 2 | 25 | 25 | May | 2021
2015 | 13226.8224 | 9815.423 | 85 | 1448.3148 | 34.76% | 34.7555 | -9.397e-06% |  |  | 0 | 0 | [14 empty] | 2015 | 2015 | 0 | 0 |  | Higgins | 3 | 36 | 33 | May | 2021
2016 | 13226.8224 | 9924.423 | 109 | 1317.5148 | 33.28% | 33.2755 | -9.904e-06% |  |  | 0 | 0 | [14 empty] | 2016 | 2016 | 0 | 75 | 40 | Higgins | 4 | 35 | 30 | May | 2021
2017 | 12681.8224 | 9889.423 | -35 | 814.5148 | 28.24% | 28.2362 | -8.332e-06% | Suwannee / Scherer / Franklin |  | -545 | 0 |  |  | -133 | [5 empty] | -412 | [5 empty] | 2017 | 2017 | 75 | 0 | 40 |  |  | 190 | 161
2018 | 12681.8224 | 10003.42 | 113.997 | 677.7184 | 26.77% | 26.7749 | -1.3e-05% |  |  | 0 | 0 | [14 empty] | 2018 | 2018 | 0 | 0 | 40 | Turner | 1 | 13 | 10 | May | 2021
2019 | 12681.8224 | 10369.42 | 366 | 238.5184 | 22.3% | 22.3002 | -3.451e-07% |  |  | 0 | 0 | [14 empty] | 2019 | 2019 | 0 | 75 | 0 | Turner | 2 | 13 | 10 | May | 2021
2020 | 12681.8224 | 10506.42 | 137 | 74.1184 | 20.71% | 20.7055 | -1.181e-05% |  |  | 0 | 0 | [14 empty] | 2020 | 2020 | 0 | 0 | 0 |  |  | 26 | 20
2021 | 12887.1224 | 10651.43 | 145.01 | 105.4064 | 20.99% | 20.9897 | -5.142e-05% |  | CT | 0 | 205.3 |  | 205.3 | [12 empty] | 2021 | 2021 | 0 | 0 | 0
2022 | 13776.1224 | 10794.43 | 143 | 822.8064 | 27.62% | 27.6226 | -5.098e-05% | Peakers | LEVY 1 | -231 | 1120 | -231 | [6 empty] | 1120 | [6 empty] | 2022 | 2022 | 0 | 75 | 0 | Rio Pinar |  | 15 | 12 | May | 2021
2023 | 14896.1224 | 10941.43 | 147 | 1766.4064 | 36.14% | 36.1442 | -2.947e-05% |  | LEVY 2 | 0 | 1120 | [7 empty] | 1120 | [6 empty] | 2023 | 2023 | 0 | 0 | 0 |  |  | 15 | 12
2024 | 14816.9224 | 11092.42 | 150.99 | 1506.0184 | 33.58% | 33.5769 | 5.484e-05% | ORLANDO |  | -79.2 | 0 | [12 empty] | -79.2 |  | 2024 | 2024 | 0 | 0 | 0
2025 | 14182.3694 | 11247.43 | 155.01 | 685.4534 | 26.09% | 26.0944 | -4.868e-05% | Shady Hills / CR2 / MULBERRY | CC2X1 G | -1509.953 | 875.4 |  |  | -874 |  |  | 875.4 |  |  | -520.953 |  |  |  | -115 |  | 2025 | 2025 | 0 | 75 | 0
2026 | 14108.3694 | 11395.42 | 147.99 | 433.8654 | 23.81% | 23.8073 | 3.647e-05% | CR1 / ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026 | 2026 | 0 | 0 | 0 | Suwannee | 1 | 30 | 30 | May | 2016
2027 | 14108.3694 | 11549.42 | 154 | 249.0654 | 22.16% | 22.1565 | 3.868e-05% |  |  | 0 | 0 | [14 empty] | 2027 | 2027 | 0 | 75 | 0 | Suwannee | 2 | 30 | 30 | May | 2016
2028 | 14316.611 | 11706.42 | 157 | 268.907 | 22.3% | 22.297 | 5.997e-05% | Vandolah Reliant | CC2X1 G | -667.1584 | 875.4 | [5 empty] | 875.4 |  |  | -667.1584 | [5 empty] | 2028 | 2028 | 0 | 0 | 0 | Suwannee | 3 | 73 | 71 | May | 2016
2029 | 14386.611 | 11860.42 | 154 | 154.107 | 21.3% | 20.7091 | 0.5902% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2029 | 2029 | 0 | 75 | 0 |  |  | 133 | 131
2030 | 14521.911 | 12017.42 | 157 | 101.007 | 20.84% | 20.8405 | 2.487e-05% |  | CT | -70 | 205.3 |  | 205.3 | [6 empty] | -70 | [5 empty] | 2030
2031 | 14591.911 | 12171.42 | 154 | -13.793 | 19.89% | 19.8866 | 2.715e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2030
2032 | 15397.311 | 12325.42 | 154 | 606.807 | 24.92% | 24.9232 | 2.56e-05% |  | CC2X1 G | -70 | 875.4 | [5 empty] | 875.4 |  |  | -70 | [5 empty] | 2030
2033 | 15397.311 | 12479.42 | 154 | 422.007 | 23.38% | 23.3816 | 2.35e-05% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 15397.311 | 12633.42 | 154 | 237.207 | 21.88% | 21.8776 | 1.509e-05% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 15397.311 | 12787.42 | 154 | 52.407 | 20.41% | 20.4098 | 2.248e-05% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 15467.311 | 12941.42 | 154 | -62.393 | 19.52% | 19.5179 | 2.135e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2030
Summer | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Summer
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year
2011 | 11697.33 | 8747.423 |  | 1200.4224 | 33.72% | 33.7232 | -5.192e-06% | TECO | Vandolah Reliant / CR3 Uprate | -70 | 158.05 | [7 empty] | 4 | -70 | 154.05 |  |  |  |  | 2011
2012 | 12014.15 | 8858.423 | 111 | 1384.0424 | 35.62% | 35.624 | -2.301e-05% |  | Vandolah NSG | -308.1 | 624.92 | [8 empty] | -308.1 | 624.92 |  |  |  |  | 2012
2013 | 12054.702 | 8918.423 | 60 | 1352.5944 | 35.17% | 35.1663 | -2.434e-05% | Lake Cogen | CR3 Uprate | -110 | 150.552 | [7 empty] | 150.552 |  |  |  |  | -110 |  | 2013
2014 | 11923.502 | 8882.423 | -36 | 1264.5944 | 34.24% | 34.2371 | -2.68e-05% | LFC / El Dorado |  | -131.2 | 0 | [8 empty] | -131.2 | [5 empty] | 2014
2015 | 11923.502 | 8925.423 | 43 | 1212.9944 | 33.59% | 33.5904 | -2.044e-05% | Anclote 1&2 Gas Conversion |  | 0 | 0 | [14 empty] | 2015
2016 | 11380.502 | 8834.423 | -91 | 779.1944 | 28.82% | 28.82 | -1.934e-05% | Suwannee / Scherer / Franklin |  | -543 | 0 |  |  | -131 | [5 empty] | -412 | [5 empty] | 2016
2017 | 11380.502 | 8891.423 | 57 | 710.7944 | 27.99% | 27.9942 | -2.203e-05% |  |  | 0 | 0 | [14 empty] | 2017
2018 | 11380.502 | 8948.423 | 57 | 642.3944 | 27.18% | 27.1789 | -2.402e-05% |  |  | 0 | 0 | [14 empty] | 2018
2019 | 11380.502 | 9268.423 | 320 | 258.3944 | 22.79% | 22.7879 | -1.962e-05% |  |  | 0 | 0 | [14 empty] | 2019
2020 | 11558.002 | 9354.423 | 86 | 332.6944 | 23.56% | 23.5567 | -0.0001235% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2020
2021 | 12457.002 | 9446.423 | 92 | 1121.2944 | 31.87% | 31.8702 | -0.0001278% | Peakers | LEVY 1 | -193 | 1092 | -193 | [6 empty] | 1092 | [6 empty] | 2021
2022 | 12457.002 | 9540.423 | 94 | 1008.4944 | 30.57% | 30.5709 | -0.0001286% |  |  | 0 | 0 | [14 empty] | 2022
2023 | 13549.002 | 9639.423 | 99 | 1981.6944 | 40.56% | 40.5583 | -0.0001236% |  | LEVY 2 | 0 | 1092 | [7 empty] | 1092 | [6 empty] | 2023
2024 | 13263.208 | 9739.423 | 100 | 1575.9004 | 36.18% | 36.1807 | -9.589e-05% | Shady Hills / CR1 / ORLANDO | CC2X1 G | -1052.684 | 766.89 |  |  | -494 |  |  | 766.89 |  |  | -479.484 |  |  |  | -79.2 |  | 2024
2025 | 12773.208 | 9842.423 | 103 | 962.3004 | 29.78% | 29.7772 | -0.0001019% | CR2 / MULBERRY |  | -490 | 0 |  |  | -375 | [9 empty] | -115 |  | 2025
2026 | 12699.208 | 9947.423 | 105 | 762.3004 | 27.66% | 27.6634 | -9.469e-05% | ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026
2027 | 12841.178 | 10051.42 | 103.997 | 779.474 | 27.75% | 27.7549 | -5.551e-05% | Vandolah Reliant | CC2X1 G | -624.92 | 766.89 | [5 empty] | 766.89 |  |  | -624.92 | [5 empty] | 2027
2028 | 12841.178 | 10156.42 | 105 | 653.474 | 26.43% | 26.4342 | -6.216e-05% |  |  | 0 | 0 | [14 empty] | 2028
2029 | 13018.678 | 10261.42 | 105 | 704.974 | 26.87% | 26.8703 | -0.0001492% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2029
2030 | 13018.678 | 10368.42 | 107 | 576.574 | 25.56% | 25.5611 | -0.0002034% |  |  | 0 | 0 | [14 empty] | 2030
2031 | 13785.568 | 10473.62 | 105.2 | 1217.224 | 31.62% | 31.622 | -0.0001921% |  | CC2X1 G | 0 | 766.89 | [5 empty] | 766.89 | [8 empty] | 2030
2032 | 13785.568 | 10578.82 | 105.2 | 1090.984 | 30.31% | 30.3131 | -0.0001918% |  |  | 0 | 0 | [14 empty] | 2030
2033 | 13785.568 | 10684.02 | 105.2 | 964.744 | 29.03% | 29.03 | -0.0001853% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 13785.568 | 10789.22 | 105.2 | 838.504 | 27.77% | 27.7719 | -0.0001868% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 13785.568 | 10894.42 | 105.2 | 712.264 | 26.54% | 26.5381 | -0.000181% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 13785.568 | 10999.62 | 105.2 | 586.024 | 25.33% | 25.3279 | -0.000185% |  |  | 0 | 0 | [14 empty] | 2030

## RMargin_Calculations_LP
Winter | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Winter |  | Renewables |  |  | Peaker and Suwannee Retirements
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year | (MW) | SUWBIOM | SOLAR_ST | BIOMASS |  |  | Winter | Summer
2011 | 12876.22 | 9577.423 |  | 1383.3124 | 34.44% | 34.4435 | -1.81e-05% | CR4 Der / Miller UPS | Vandolah Reliant / Scherer / Franklin / CR3 Uprate | -434 | 571.58 |  |  | -20 | [5 empty] | -414 | 571.58 |  |  |  |  | 2011 | 2011 | 0 | 0 | 0 | Avon Park | 1 | 34 | 24 | May | 2021
2012 | 12969.472 | 9640.423 | 63 | 1400.9644 | 34.53% | 34.5322 | -1.941e-06% | TECO | Vandolah Reliant | -70 | 163.252 | [7 empty] | 3.672 | -70 | 159.58 |  |  |  |  | 2012 | 2012 | 0 | 0 | 0 | Avon Park | 2 | 35 | 24 | May | 2021
2013 | 13339.4984 | 9716.423 | 76 | 1679.7908 | 37.29% | 37.2882 | -5.953e-05% | Vandolah Reliant | Vandolah NSG | -319.16 | 689.1864 | [7 empty] | 22.028 | -319.16 | 667.1584 |  |  |  |  | 2013 | 2013 | 0 | 0 | 0 | Higgins | 1 | 25 | 25 | May | 2021
2014 | 13098.2984 | 9730.423 | 14 | 1421.7908 | 34.61% | 34.6119 | -6.124e-05% | Lake Cogen / LFC / El Dorado |  | -241.2 | 0 | [12 empty] | -241.2 |  | 2014 | 2014 | 0 | 0 | 40 | Higgins | 2 | 25 | 25 | May | 2021
2015 | 13098.2984 | 9815.423 | 85 | 1319.7908 | 33.45% | 33.4462 | -5.807e-05% |  |  | 0 | 0 | [14 empty] | 2015 | 2015 | 0 | 0 |  | Higgins | 3 | 36 | 33 | May | 2021
2016 | 13098.2984 | 9924.423 | 109 | 1188.9908 | 31.98% | 31.9805 | -5.733e-05% |  |  | 0 | 0 | [14 empty] | 2016 | 2016 | 0 | 75 | 40 | Higgins | 4 | 35 | 30 | May | 2021
2017 | 12553.2984 | 9889.423 | -35 | 685.9908 | 26.94% | 26.9367 | -5.904e-05% | Suwannee / Scherer / Franklin |  | -545 | 0 |  |  | -133 | [5 empty] | -412 | [5 empty] | 2017 | 2017 | 75 | 0 | 40 |  |  | 190 | 161
2018 | 12553.2984 | 10003.42 | 113.997 | 549.1944 | 25.49% | 25.4901 | -5.36e-05% |  |  | 0 | 0 | [14 empty] | 2018 | 2018 | 0 | 0 | 40 | Turner | 1 | 13 | 10 | May | 2021
2019 | 12553.2984 | 10369.42 | 366 | 109.9944 | 21.06% | 21.0608 | -4.25e-05% |  |  | 0 | 0 | [14 empty] | 2019 | 2019 | 0 | 75 | 0 | Turner | 2 | 13 | 10 | May | 2021
2020 | 12758.5984 | 10506.42 | 137 | 150.8944 | 21.44% | 21.4363 | -4.862e-05% |  | CT | 0 | 205.3 |  | 205.3 | [12 empty] | 2020 | 2020 | 0 | 0 | 0 |  |  | 26 | 20
2021 | 12758.5984 | 10651.43 | 145.01 | -23.1176 | 19.78% | 19.7831 | -9.752e-05% |  |  | 0 | 0 | [14 empty] | 2021 | 2021 | 0 | 0 | 0
2022 | 13647.5984 | 10794.43 | 143 | 694.2824 | 26.43% | 26.432 | -0.0001021% | Peakers | LEVY 1 | -231 | 1120 | -231 | [6 empty] | 1120 | [6 empty] | 2022 | 2022 | 0 | 75 | 0 | Rio Pinar |  | 15 | 12 | May | 2021
2023 | 14767.5984 | 10941.43 | 147 | 1637.8824 | 34.97% | 34.9696 | -7.397e-05% |  | LEVY 2 | 0 | 1120 | [7 empty] | 1120 | [6 empty] | 2023 | 2023 | 0 | 0 | 0 |  |  | 15 | 12
2024 | 14688.3984 | 11092.42 | 150.99 | 1377.4944 | 32.42% | 32.4183 | 9.731e-06% | ORLANDO |  | -79.2 | 0 | [12 empty] | -79.2 |  | 2024 | 2024 | 0 | 0 | 0
2025 | 14053.8454 | 11247.43 | 155.01 | 556.9294 | 24.95% | 24.9517 | -8.528e-05% | Shady Hills / CR2 / MULBERRY | CC2X1 G | -1509.953 | 875.4 |  |  | -874 |  |  | 875.4 |  |  | -520.953 |  |  |  | -115 |  | 2025 | 2025 | 0 | 75 | 0
2026 | 13979.8454 | 11395.42 | 147.99 | 305.3414 | 22.68% | 22.6795 | -1.016e-05% | CR1 / ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026 | 2026 | 0 | 0 | 0 | Suwannee | 1 | 30 | 30 | May | 2016
2027 | 13979.8454 | 11549.42 | 154 | 120.5414 | 21.04% | 21.0437 | 8.958e-07% |  |  | 0 | 0 | [14 empty] | 2027 | 2027 | 0 | 75 | 0 | Suwannee | 2 | 30 | 30 | May | 2016
2028 | 14188.087 | 11706.42 | 157 | 140.383 | 21.2% | 21.1992 | 2.668e-05% | Vandolah Reliant | CC2X1 G | -667.1584 | 875.4 | [5 empty] | 875.4 |  |  | -667.1584 | [5 empty] | 2028 | 2028 | 0 | 0 | 0 | Suwannee | 3 | 73 | 71 | May | 2016
2029 | 14258.087 | 11860.42 | 154 | 25.583 | 20.22% | 20.2157 | 6.244e-07% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2029 | 2029 | 0 | 75 | 0 |  |  | 133 | 131
2030 | 14393.387 | 12017.42 | 157 | -27.517 | 19.77% | 19.771 | -1.594e-05% |  | CT | -70 | 205.3 |  | 205.3 | [6 empty] | -70 | [5 empty] | 2030
2031 | 14668.687 | 12171.42 | 154 | 62.983 | 20.52% | 20.5175 | -1.367e-05% |  | CT - PURCH 70MW | 0 | 275.3 |  | 205.3 | [7 empty] | 70 |  |  |  |  | 2030
2032 | 15474.087 | 12325.42 | 154 | 683.583 | 25.55% | 25.5461 | -1.662e-05% |  | CC2X1 G | -70 | 875.4 | [5 empty] | 875.4 |  |  | -70 | [5 empty] | 2030
2033 | 15474.087 | 12479.42 | 154 | 498.783 | 24% | 23.9969 | -1.56e-05% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 15474.087 | 12633.42 | 154 | 313.983 | 22.49% | 22.4854 | -1.349e-05% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 15474.087 | 12787.42 | 154 | 129.183 | 21.01% | 21.0102 | -1.494e-05% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 15544.087 | 12941.42 | 154 | 14.383 | 20.11% | 20.1111 | -1.073e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2030
Summer | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Summer
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year
2011 | 11697.33 | 8747.423 |  | 1200.4224 | 33.72% | 33.7232 | -5.192e-06% | TECO | Vandolah Reliant / CR3 Uprate | -70 | 158.05 | [7 empty] | 4 | -70 | 154.05 |  |  |  |  | 2011
2012 | 12014.15 | 8858.423 | 111 | 1384.0424 | 35.62% | 35.624 | -2.301e-05% |  | Vandolah NSG | -308.1 | 624.92 | [8 empty] | -308.1 | 624.92 |  |  |  |  | 2012
2013 | 11926.178 | 8918.423 | 60 | 1224.0704 | 33.73% | 33.7253 | -6.114e-05% | Lake Cogen |  | -110 | 22.028 | [7 empty] | 22.028 |  |  |  |  | -110 |  | 2013
2014 | 11794.978 | 8882.423 | -36 | 1136.0704 | 32.79% | 32.7902 | -6.432e-05% | LFC / El Dorado |  | -131.2 | 0 | [8 empty] | -131.2 | [5 empty] | 2014
2015 | 11794.978 | 8925.423 | 43 | 1084.4704 | 32.15% | 32.1504 | -6.701e-05% |  |  | 0 | 0 | [14 empty] | 2015
2016 | 11251.978 | 8834.423 | -91 | 650.6704 | 27.37% | 27.3652 | -5.856e-05% | Suwannee / Scherer / Franklin |  | -543 | 0 |  |  | -131 | [5 empty] | -412 | [5 empty] | 2016
2017 | 11251.978 | 8891.423 | 57 | 582.2704 | 26.55% | 26.5487 | -6.495e-05% |  |  | 0 | 0 | [14 empty] | 2017
2018 | 11251.978 | 8948.423 | 57 | 513.8704 | 25.74% | 25.7426 | -5.944e-05% |  |  | 0 | 0 | [14 empty] | 2018
2019 | 11429.478 | 9268.423 | 320 | 307.3704 | 23.32% | 23.3165 | -0.0001618% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2019
2020 | 11429.478 | 9354.423 | 86 | 204.1704 | 22.18% | 22.1828 | -0.0001618% |  |  | 0 | 0 | [14 empty] | 2020
2021 | 12328.478 | 9446.423 | 92 | 992.7704 | 30.51% | 30.5097 | -0.0001651% | Peakers | LEVY 1 | -193 | 1092 | -193 | [6 empty] | 1092 | [6 empty] | 2021
2022 | 12328.478 | 9540.423 | 94 | 879.9704 | 29.22% | 29.2238 | -0.0001606% |  |  | 0 | 0 | [14 empty] | 2022
2023 | 13420.478 | 9639.423 | 99 | 1853.1704 | 39.22% | 39.2251 | -0.00016% |  | LEVY 2 | 0 | 1092 | [7 empty] | 1092 | [6 empty] | 2023
2024 | 13134.684 | 9739.423 | 100 | 1447.3764 | 34.86% | 34.8611 | -0.0001323% | Shady Hills / CR1 / ORLANDO | CC2X1 G | -1052.684 | 766.89 |  |  | -494 |  |  | 766.89 |  |  | -479.484 |  |  |  | -79.2 |  | 2024
2025 | 12644.684 | 9842.423 | 103 | 833.7764 | 28.47% | 28.4714 | -0.0001386% | CR2 / MULBERRY |  | -490 | 0 |  |  | -375 | [9 empty] | -115 |  | 2025
2026 | 12570.684 | 9947.423 | 105 | 633.7764 | 26.37% | 26.3714 | -0.0001378% | ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026
2027 | 12712.654 | 10051.42 | 103.997 | 650.95 | 26.48% | 26.4763 | -9.062e-05% | Vandolah Reliant | CC2X1 G | -624.92 | 766.89 | [5 empty] | 766.89 |  |  | -624.92 | [5 empty] | 2027
2028 | 12712.654 | 10156.42 | 105 | 524.95 | 25.17% | 25.1687 | -9.805e-05% |  |  | 0 | 0 | [14 empty] | 2028
2029 | 12890.154 | 10261.42 | 105 | 576.45 | 25.62% | 25.6178 | -0.0001864% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2029
2030 | 13067.654 | 10368.42 | 107 | 625.55 | 26.03% | 26.0336 | -0.000326% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2030
2031 | 13834.544 | 10473.62 | 105.2 | 1266.2 | 32.09% | 32.0897 | -0.0003192% |  | CC2X1 G | 0 | 766.89 | [5 empty] | 766.89 | [8 empty] | 2030
2032 | 13834.544 | 10578.82 | 105.2 | 1139.96 | 30.78% | 30.7762 | -0.000309% |  |  | 0 | 0 | [14 empty] | 2030
2033 | 13834.544 | 10684.02 | 105.2 | 1013.72 | 29.49% | 29.4885 | -0.0003011% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 13834.544 | 10789.22 | 105.2 | 887.48 | 28.23% | 28.2259 | -0.0003122% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 13834.544 | 10894.42 | 105.2 | 761.24 | 26.99% | 26.9877 | -0.0003097% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 13834.544 | 10999.62 | 105.2 | 635 | 25.77% | 25.7732 | -0.0003033% |  |  | 0 | 0 | [14 empty] | 2030
12819.41

## RMargin_Calculations_LP_HP
Winter | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Winter |  | Renewables |  |  | Peaker and Suwannee Retirements
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year | (MW) | SUWBIOM | SOLAR_ST | BIOMASS |  |  | Winter | Summer
2011 | 12876.22 | 9577.423 |  | 1383.3124 | 34.44% | 34.4435 | -1.81e-05% | CR4 Der / Miller UPS | Vandolah Reliant / Scherer / Franklin / CR3 Uprate | -434 | 571.58 |  |  | -20 | [5 empty] | -414 | 571.58 |  |  |  |  | 2011 | 2011 | 0 | 0 | 0 | Avon Park | 1 | 34 | 24 | May | 2021
2012 | 12969.472 | 9640.423 | 63 | 1400.9644 | 34.53% | 34.5322 | -1.941e-06% | TECO | Vandolah Reliant | -70 | 163.252 | [7 empty] | 3.672 | -70 | 159.58 |  |  |  |  | 2012 | 2012 | 0 | 0 | 0 | Avon Park | 2 | 35 | 24 | May | 2021
2013 | 13332.1584 | 9716.423 | 76 | 1672.4508 | 37.21% | 37.2126 | -2.174e-05% | Vandolah Reliant | Vandolah NSG | -319.16 | 681.8464 | [7 empty] | 14.688 | -319.16 | 667.1584 |  |  |  |  | 2013 | 2013 | 0 | 0 | 0 | Higgins | 1 | 25 | 25 | May | 2021
2014 | 13090.9584 | 9730.423 | 14 | 1414.4508 | 34.54% | 34.5364 | -1.476e-05% | Lake Cogen / LFC / El Dorado |  | -241.2 | 0 | [12 empty] | -241.2 |  | 2014 | 2014 | 0 | 0 | 40 | Higgins | 2 | 25 | 25 | May | 2021
2015 | 13090.9584 | 9815.423 | 85 | 1312.4508 | 33.37% | 33.3713 | -1.834e-05% |  |  | 0 | 0 | [14 empty] | 2015 | 2015 | 0 | 0 |  | Higgins | 3 | 36 | 33 | May | 2021
2016 | 13090.9584 | 9924.423 | 109 | 1181.6508 | 31.91% | 31.9065 | -1.629e-05% |  |  | 0 | 0 | [14 empty] | 2016 | 2016 | 0 | 75 | 40 | Higgins | 4 | 35 | 30 | May | 2021
2017 | 12545.9584 | 9889.423 | -35 | 678.6508 | 26.86% | 26.8624 | -1.975e-05% | Suwannee / Scherer / Franklin |  | -545 | 0 |  |  | -133 | [5 empty] | -412 | [5 empty] | 2017 | 2017 | 75 | 0 | 40 |  |  | 190 | 161
2018 | 12545.9584 | 10003.42 | 113.997 | 541.8544 | 25.42% | 25.4167 | -1.851e-05% |  |  | 0 | 0 | [14 empty] | 2018 | 2018 | 0 | 0 | 40 | Turner | 1 | 13 | 10 | May | 2021
2019 | 12545.9584 | 10369.42 | 366 | 102.6544 | 20.99% | 20.99 | -7.562e-06% |  |  | 0 | 0 | [14 empty] | 2019 | 2019 | 0 | 75 | 0 | Turner | 2 | 13 | 10 | May | 2021
2020 | 12751.2584 | 10506.42 | 137 | 143.5544 | 21.37% | 21.3664 | -1.066e-05% |  | CT | 0 | 205.3 |  | 205.3 | [12 empty] | 2020 | 2020 | 0 | 0 | 0 |  |  | 26 | 20
2021 | 12751.2584 | 10651.43 | 145.01 | -30.4576 | 19.71% | 19.7141 | -5.846e-05% |  |  | 0 | 0 | [14 empty] | 2021 | 2021 | 0 | 0 | 0
2022 | 13640.2584 | 10794.43 | 143 | 686.9424 | 26.36% | 26.3639 | -6.012e-05% | Peakers | LEVY 1 | -231 | 1120 | -231 | [6 empty] | 1120 | [6 empty] | 2022 | 2022 | 0 | 75 | 0 | Rio Pinar |  | 15 | 12 | May | 2021
2023 | 14760.2584 | 10941.43 | 147 | 1630.5424 | 34.9% | 34.9025 | -3.844e-05% |  | LEVY 2 | 0 | 1120 | [7 empty] | 1120 | [6 empty] | 2023 | 2023 | 0 | 0 | 0 |  |  | 15 | 12
2024 | 14681.0584 | 11092.42 | 150.99 | 1370.1544 | 32.35% | 32.3521 | 4.842e-05% | ORLANDO |  | -79.2 | 0 | [12 empty] | -79.2 |  | 2024 | 2024 | 0 | 0 | 0
2025 | 14046.5054 | 11247.43 | 155.01 | 549.5894 | 24.89% | 24.8864 | -5.463e-05% | Shady Hills / CR2 / MULBERRY | CC2X1 G | -1509.953 | 875.4 |  |  | -874 |  |  | 875.4 |  |  | -520.953 |  |  |  | -115 |  | 2025 | 2025 | 0 | 75 | 0
2026 | 13972.5054 | 11395.42 | 147.99 | 298.0014 | 22.62% | 22.6151 | 2.8e-05% | CR1 / ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026 | 2026 | 0 | 0 | 0 | Suwannee | 1 | 30 | 30 | May | 2016
2027 | 13972.5054 | 11549.42 | 154 | 113.2014 | 20.98% | 20.9801 | 3.792e-05% |  |  | 0 | 0 | [14 empty] | 2027 | 2027 | 0 | 75 | 0 | Suwannee | 2 | 30 | 30 | May | 2016
2028 | 14180.747 | 11706.42 | 157 | 133.043 | 21.14% | 21.1364 | 5.604e-05% | Vandolah Reliant | CC2X1 G | -667.1584 | 875.4 | [5 empty] | 875.4 |  |  | -667.1584 | [5 empty] | 2028 | 2028 | 0 | 0 | 0 | Suwannee | 3 | 73 | 71 | May | 2016
2029 | 14250.747 | 11860.42 | 154 | 18.243 | 20.15% | 20.1538 | 3.411e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2029 | 2029 | 0 | 75 | 0 |  |  | 133 | 131
2030 | 14386.047 | 12017.42 | 157 | -34.857 | 19.71% | 19.7099 | 1.606e-05% |  | CT | -70 | 205.3 |  | 205.3 | [6 empty] | -70 | [5 empty] | 2030
2031 | 14661.347 | 12171.42 | 154 | 55.643 | 20.46% | 20.4571 | 2.112e-05% |  | CT - PURCH 70MW | 0 | 275.3 |  | 205.3 | [7 empty] | 70 |  |  |  |  | 2030
2032 | 15466.747 | 12325.42 | 154 | 676.243 | 25.49% | 25.4866 | 1.165e-05% |  | CC2X1 G | -70 | 875.4 | [5 empty] | 875.4 |  |  | -70 | [5 empty] | 2030
2033 | 15466.747 | 12479.42 | 154 | 491.443 | 23.94% | 23.938 | 1.757e-05% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 15466.747 | 12633.42 | 154 | 306.643 | 22.43% | 22.4272 | 1.665e-05% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 15466.747 | 12787.42 | 154 | 121.843 | 20.95% | 20.9528 | 1.49e-05% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 15536.747 | 12941.42 | 154 | 7.043 | 20.05% | 20.0544 | 1.216e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2030
Summer | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Summer
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year
2011 | 11697.33 | 8747.423 |  | 1200.4224 | 33.72% | 33.7232 | -5.192e-06% | TECO | Vandolah Reliant / CR3 Uprate | -70 | 158.05 | [7 empty] | 4 | -70 | 154.05 |  |  |  |  | 2011
2012 | 12014.15 | 8858.423 | 111 | 1384.0424 | 35.62% | 35.624 | -2.301e-05% |  | Vandolah NSG | -308.1 | 624.92 | [8 empty] | -308.1 | 624.92 |  |  |  |  | 2012
2013 | 11918.838 | 8918.423 | 60 | 1216.7304 | 33.64% | 33.6429 | -2.269e-05% | Lake Cogen |  | -110 | 14.688 | [7 empty] | 14.688 |  |  |  |  | -110 |  | 2013
2014 | 11787.638 | 8882.423 | -36 | 1128.7304 | 32.71% | 32.7075 | -1.943e-05% | LFC / El Dorado |  | -131.2 | 0 | [8 empty] | -131.2 | [5 empty] | 2014
2015 | 11787.638 | 8925.423 | 43 | 1077.1304 | 32.07% | 32.0681 | -2.401e-05% |  |  | 0 | 0 | [14 empty] | 2015
2016 | 11244.638 | 8834.423 | -91 | 643.3304 | 27.28% | 27.2821 | -2.265e-05% | Suwannee / Scherer / Franklin |  | -543 | 0 |  |  | -131 | [5 empty] | -412 | [5 empty] | 2016
2017 | 11244.638 | 8891.423 | 57 | 574.9304 | 26.47% | 26.4661 | -1.641e-05% |  |  | 0 | 0 | [14 empty] | 2017
2018 | 11244.638 | 8948.423 | 57 | 506.5304 | 25.66% | 25.6606 | -2.506e-05% |  |  | 0 | 0 | [14 empty] | 2018
2019 | 11422.138 | 9268.423 | 320 | 300.0304 | 23.24% | 23.2372 | -0.0001254% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2019
2020 | 11422.138 | 9354.423 | 86 | 196.8304 | 22.1% | 22.1043 | -0.0001274% |  |  | 0 | 0 | [14 empty] | 2020
2021 | 12321.138 | 9446.423 | 92 | 985.4304 | 30.43% | 30.4319 | -0.0001265% | Peakers | LEVY 1 | -193 | 1092 | -193 | [6 empty] | 1092 | [6 empty] | 2021
2022 | 12321.138 | 9540.423 | 94 | 872.6304 | 29.15% | 29.1468 | -0.0001264% |  |  | 0 | 0 | [14 empty] | 2022
2023 | 13413.138 | 9639.423 | 99 | 1845.8304 | 39.15% | 39.1489 | -0.0001156% |  | LEVY 2 | 0 | 1092 | [7 empty] | 1092 | [6 empty] | 2023
2024 | 13127.344 | 9739.423 | 100 | 1440.0364 | 34.79% | 34.7857 | -8.613e-05% | Shady Hills / CR1 / ORLANDO | CC2X1 G | -1052.684 | 766.89 |  |  | -494 |  |  | 766.89 |  |  | -479.484 |  |  |  | -79.2 |  | 2024
2025 | 12637.344 | 9842.423 | 103 | 826.4364 | 28.4% | 28.3968 | -9.369e-05% | CR2 / MULBERRY |  | -490 | 0 |  |  | -375 | [9 empty] | -115 |  | 2025
2026 | 12563.344 | 9947.423 | 105 | 626.4364 | 26.3% | 26.2976 | -9.577e-05% | ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026
2027 | 12705.314 | 10051.42 | 103.997 | 643.61 | 26.4% | 26.4032 | -5.513e-05% | Vandolah Reliant | CC2X1 G | -624.92 | 766.89 | [5 empty] | 766.89 |  |  | -624.92 | [5 empty] | 2027
2028 | 12705.314 | 10156.42 | 105 | 517.61 | 25.1% | 25.0964 | -5.761e-05% |  |  | 0 | 0 | [14 empty] | 2028
2029 | 12882.814 | 10261.42 | 105 | 569.11 | 25.55% | 25.5463 | -0.0001465% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2029
2030 | 13060.314 | 10368.42 | 107 | 618.21 | 25.96% | 25.9627 | -0.0002879% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2030
2031 | 13827.204 | 10473.62 | 105.2 | 1258.86 | 32.02% | 32.0196 | -0.00028% |  | CC2X1 G | 0 | 766.89 | [5 empty] | 766.89 | [8 empty] | 2030
2032 | 13827.204 | 10578.82 | 105.2 | 1132.62 | 30.71% | 30.7068 | -0.0002729% |  |  | 0 | 0 | [14 empty] | 2030
2033 | 13827.204 | 10684.02 | 105.2 | 1006.38 | 29.42% | 29.4198 | -0.0002718% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 13827.204 | 10789.22 | 105.2 | 880.14 | 28.16% | 28.1579 | -0.0002831% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 13827.204 | 10894.42 | 105.2 | 753.9 | 26.92% | 26.9203 | -0.0002737% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 13827.204 | 10999.62 | 105.2 | 627.66 | 25.71% | 25.7065 | -0.0002629% |  |  | 0 | 0 | [14 empty] | 2030
12819.41

## RMargin_Calculations_NP
Winter | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Winter |  | Renewables |  |  | Peaker and Suwannee Retirements
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year | (MW) | SUWBIOM | SOLAR_ST | BIOMASS |  |  | Winter | Summer
2011 | 12876.22 | 9577.423 |  | 1383.3124 | 34.44% | 34.4435 | -1.81e-05% | CR4 Der / Miller UPS | Vandolah Reliant / Scherer / Franklin / CR3 Uprate | -434 | 571.58 |  |  | -20 | [5 empty] | -414 | 571.58 |  |  |  |  | 2011 | 2011 | 0 | 0 | 0 | Avon Park | 1 | 34 | 24 | May | 2021
2012 | 12969.472 | 9640.423 | 63 | 1400.9644 | 34.53% | 34.5322 | -1.941e-06% | TECO | Vandolah Reliant | -70 | 163.252 | [7 empty] | 3.672 | -70 | 159.58 |  |  |  |  | 2012 | 2012 | 0 | 0 | 0 | Avon Park | 2 | 35 | 24 | May | 2021
2013 | 13317.4704 | 9716.423 | 76 | 1657.7628 | 37.06% | 37.0615 | -1.848e-05% | Vandolah Reliant | Vandolah NSG | -319.16 | 667.1584 | [8 empty] | -319.16 | 667.1584 |  |  |  |  | 2013 | 2013 | 0 | 0 | 0 | Higgins | 1 | 25 | 25 | May | 2021
2014 | 13076.2704 | 9730.423 | 14 | 1399.7628 | 34.39% | 34.3854 | -1.4e-05% | Lake Cogen / LFC / El Dorado |  | -241.2 | 0 | [12 empty] | -241.2 |  | 2014 | 2014 | 0 | 0 | 40 | Higgins | 2 | 25 | 25 | May | 2021
2015 | 13076.2704 | 9815.423 | 85 | 1297.7628 | 33.22% | 33.2217 | -1.039e-05% |  |  | 0 | 0 | [14 empty] | 2015 | 2015 | 0 | 0 |  | Higgins | 3 | 36 | 33 | May | 2021
2016 | 13076.2704 | 9924.423 | 109 | 1166.9628 | 31.76% | 31.7585 | -1.482e-05% |  |  | 0 | 0 | [14 empty] | 2016 | 2016 | 0 | 75 | 40 | Higgins | 4 | 35 | 30 | May | 2021
2017 | 12531.2704 | 9889.423 | -35 | 663.9628 | 26.71% | 26.7139 | -1.206e-05% | Suwannee / Scherer / Franklin |  | -545 | 0 |  |  | -133 | [5 empty] | -412 | [5 empty] | 2017 | 2017 | 75 | 0 | 40 |  |  | 190 | 161
2018 | 12531.2704 | 10003.42 | 113.997 | 527.1664 | 25.27% | 25.2699 | -8.293e-06% |  |  | 0 | 0 | [14 empty] | 2018 | 2018 | 0 | 0 | 40 | Turner | 1 | 13 | 10 | May | 2021
2019 | 12531.2704 | 10369.42 | 366 | 87.9664 | 20.85% | 20.8483 | -4.828e-06% |  |  | 0 | 0 | [14 empty] | 2019 | 2019 | 0 | 75 | 0 | Turner | 2 | 13 | 10 | May | 2021
2020 | 12736.5704 | 10506.42 | 137 | 128.8664 | 21.23% | 21.2266 | -1.09e-05% |  | CT | 0 | 205.3 |  | 205.3 | [12 empty] | 2020 | 2020 | 0 | 0 | 0 |  |  | 26 | 20
2021 | 12736.5704 | 10651.43 | 145.01 | -45.1456 | 19.58% | 19.5762 | -5.544e-05% |  |  | 0 | 0 | [14 empty] | 2021 | 2021 | 0 | 0 | 0
2022 | 13625.5704 | 10794.43 | 143 | 672.2544 | 26.23% | 26.2279 | -6.03e-05% | Peakers | LEVY 1 | -231 | 1120 | -231 | [6 empty] | 1120 | [6 empty] | 2022 | 2022 | 0 | 75 | 0 | Rio Pinar |  | 15 | 12 | May | 2021
2023 | 14745.5704 | 10941.43 | 147 | 1615.8544 | 34.77% | 34.7683 | -4.049e-05% |  | LEVY 2 | 0 | 1120 | [7 empty] | 1120 | [6 empty] | 2023 | 2023 | 0 | 0 | 0 |  |  | 15 | 12
2024 | 14666.3704 | 11092.42 | 150.99 | 1355.4664 | 32.22% | 32.2197 | 5.367e-05% | ORLANDO |  | -79.2 | 0 | [12 empty] | -79.2 |  | 2024 | 2024 | 0 | 0 | 0
2025 | 14031.8174 | 11247.43 | 155.01 | 534.9014 | 24.76% | 24.7558 | -4.446e-05% | Shady Hills / CR2 / MULBERRY | CC2X1 G | -1509.953 | 875.4 |  |  | -874 |  |  | 875.4 |  |  | -520.953 |  |  |  | -115 |  | 2025 | 2025 | 0 | 75 | 0
2026 | 13957.8174 | 11395.42 | 147.99 | 283.3134 | 22.49% | 22.4862 | 3.411e-05% | CR1 / ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026 | 2026 | 0 | 0 | 0 | Suwannee | 1 | 30 | 30 | May | 2016
2027 | 13957.8174 | 11549.42 | 154 | 98.5134 | 20.85% | 20.8529 | 4.27e-05% |  |  | 0 | 0 | [14 empty] | 2027 | 2027 | 0 | 75 | 0 | Suwannee | 2 | 30 | 30 | May | 2016
2028 | 14166.059 | 11706.42 | 157 | 118.355 | 21.01% | 21.011 | 5.643e-05% | Vandolah Reliant | CC2X1 G | -667.1584 | 875.4 | [5 empty] | 875.4 |  |  | -667.1584 | [5 empty] | 2028 | 2028 | 0 | 0 | 0 | Suwannee | 3 | 73 | 71 | May | 2016
2029 | 14236.059 | 11860.42 | 154 | 3.555 | 20.03% | 20.0299 | 4.364e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2029 | 2029 | 0 | 75 | 0 |  |  | 133 | 131
2030 | 14371.359 | 12017.42 | 157 | -49.545 | 19.59% | 19.5877 | 2.349e-05% |  | CT | -70 | 205.3 |  | 205.3 | [6 empty] | -70 | [5 empty] | 2030
2031 | 14646.659 | 12171.42 | 154 | 40.955 | 20.34% | 20.3365 | 2.498e-05% |  | CT - PURCH 70MW | 0 | 275.3 |  | 205.3 | [7 empty] | 70 |  |  |  |  | 2030
2032 | 15452.059 | 12325.42 | 154 | 661.555 | 25.37% | 25.3674 | 2.33e-05% |  | CC2X1 G | -70 | 875.4 | [5 empty] | 875.4 |  |  | -70 | [5 empty] | 2030
2033 | 15452.059 | 12479.42 | 154 | 476.755 | 23.82% | 23.8203 | 1.979e-05% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 15452.059 | 12633.42 | 154 | 291.955 | 22.31% | 22.3109 | 2.359e-05% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 15452.059 | 12787.42 | 154 | 107.155 | 20.84% | 20.8379 | 2.201e-05% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 15522.059 | 12941.42 | 154 | -7.645 | 19.94% | 19.9409 | 1.611e-05% |  | PURCH 70MW | 0 | 70 | [9 empty] | 70 |  |  |  |  | 2030
Summer | [7 empty] | Retirements | Additions | Total | Total | Peakers | Peakers | Fossil | Fossil | CC | CC | Nuclear | Nuclear | PPA | PPA | Renewables | Renewables | Cogens | Cogens | Summer
Year | Firm Capacity | Peak Demand | Peak Increase | Excess Capacity | Reserve Margin | Strategist | Diff | Comments | Comments | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Capacity Retirements | Capacity Additions | Year
2011 | 11697.33 | 8747.423 |  | 1200.4224 | 33.72% | 33.7232 | -5.192e-06% | TECO | Vandolah Reliant / CR3 Uprate | -70 | 158.05 | [7 empty] | 4 | -70 | 154.05 |  |  |  |  | 2011
2012 | 12014.15 | 8858.423 | 111 | 1384.0424 | 35.62% | 35.624 | -2.301e-05% |  | Vandolah NSG | -308.1 | 624.92 | [8 empty] | -308.1 | 624.92 |  |  |  |  | 2012
2013 | 11904.15 | 8918.423 | 60 | 1202.0424 | 33.48% | 33.4782 | -2.548e-05% | Lake Cogen |  | -110 | 0 | [12 empty] | -110 |  | 2013
2014 | 11772.95 | 8882.423 | -36 | 1114.0424 | 32.54% | 32.5421 | -2.972e-05% | LFC / El Dorado |  | -131.2 | 0 | [8 empty] | -131.2 | [5 empty] | 2014
2015 | 11772.95 | 8925.423 | 43 | 1062.4424 | 31.9% | 31.9036 | -2.764e-05% |  |  | 0 | 0 | [14 empty] | 2015
2016 | 11229.95 | 8834.423 | -91 | 628.6424 | 27.12% | 27.1158 | -2.138e-05% | Suwannee / Scherer / Franklin |  | -543 | 0 |  |  | -131 | [5 empty] | -412 | [5 empty] | 2016
2017 | 11229.95 | 8891.423 | 57 | 560.2424 | 26.3% | 26.301 | -2.932e-05% |  |  | 0 | 0 | [14 empty] | 2017
2018 | 11229.95 | 8948.423 | 57 | 491.8424 | 25.5% | 25.4964 | -2.572e-05% |  |  | 0 | 0 | [14 empty] | 2018
2019 | 11407.45 | 9268.423 | 320 | 285.3424 | 23.08% | 23.0788 | -0.000129% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2019
2020 | 11407.45 | 9354.423 | 86 | 182.1424 | 21.95% | 21.9473 | -0.000134% |  |  | 0 | 0 | [14 empty] | 2020
2021 | 12306.45 | 9446.423 | 92 | 970.7424 | 30.28% | 30.2764 | -0.0001239% | Peakers | LEVY 1 | -193 | 1092 | -193 | [6 empty] | 1092 | [6 empty] | 2021
2022 | 12306.45 | 9540.423 | 94 | 857.9424 | 28.99% | 28.9928 | -0.0001318% |  |  | 0 | 0 | [14 empty] | 2022
2023 | 13398.45 | 9639.423 | 99 | 1831.1424 | 39% | 38.9965 | -0.0001299% |  | LEVY 2 | 0 | 1092 | [7 empty] | 1092 | [6 empty] | 2023
2024 | 13112.656 | 9739.423 | 100 | 1425.3484 | 34.63% | 34.6349 | -9.588e-05% | Shady Hills / CR1 / ORLANDO | CC2X1 G | -1052.684 | 766.89 |  |  | -494 |  |  | 766.89 |  |  | -479.484 |  |  |  | -79.2 |  | 2024
2025 | 12622.656 | 9842.423 | 103 | 811.7484 | 28.25% | 28.2476 | -0.0001052% | CR2 / MULBERRY |  | -490 | 0 |  |  | -375 | [9 empty] | -115 |  | 2025
2026 | 12548.656 | 9947.423 | 105 | 611.7484 | 26.15% | 26.1499 | -0.0001021% | ORANGE |  | -74 | 0 | [12 empty] | -74 |  | 2026
2027 | 12690.626 | 10051.42 | 103.997 | 628.922 | 26.26% | 26.2571 | -6.373e-05% | Vandolah Reliant | CC2X1 G | -624.92 | 766.89 | [5 empty] | 766.89 |  |  | -624.92 | [5 empty] | 2027
2028 | 12690.626 | 10156.42 | 105 | 502.922 | 24.95% | 24.9518 | -6.55e-05% |  |  | 0 | 0 | [14 empty] | 2028
2029 | 12868.126 | 10261.42 | 105 | 554.422 | 25.4% | 25.4031 | -0.0001546% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2029
2030 | 13045.626 | 10368.42 | 107 | 603.522 | 25.82% | 25.8211 | -0.0002989% |  | CT | 0 | 177.5 |  | 177.5 | [12 empty] | 2030
2031 | 13812.516 | 10473.62 | 105.2 | 1244.172 | 31.88% | 31.8794 | -0.000288% |  | CC2X1 G | 0 | 766.89 | [5 empty] | 766.89 | [8 empty] | 2030
2032 | 13812.516 | 10578.82 | 105.2 | 1117.932 | 30.57% | 30.5679 | -0.0002763% |  |  | 0 | 0 | [14 empty] | 2030
2033 | 13812.516 | 10684.02 | 105.2 | 991.692 | 29.28% | 29.2823 | -0.0002782% |  |  | 0 | 0 | [14 empty] | 2030
2034 | 13812.516 | 10789.22 | 105.2 | 865.452 | 28.02% | 28.0217 | -0.000279% |  |  | 0 | 0 | [14 empty] | 2030
2035 | 13812.516 | 10894.42 | 105.2 | 739.212 | 26.79% | 26.7855 | -0.000275% |  |  | 0 | 0 | [14 empty] | 2030
2036 | 13812.516 | 10999.62 | 105.2 | 612.972 | 25.57% | 25.5729 | -0.0002748% |  |  | 0 | 0 | [14 empty] | 2030

## Assumptions
2011 EPU Assumptions Summary | Planning Period | 2010-2036
The 2010 NOV GFF was modified by the following assumptions:
Units Retirement | Date | Winter MW | Summer MW
Suwannee River 1-3 | 2016-05-01 | 133 | 131 | MWs
Avon Park 1-2 | 2019-05-01 | 66 | 48
Higgings 1-4 | 2019-05-01 | 135 | 114
Rio Pinar | 2019-05-01 | 13 | 12
Turnet 1-2 | 2019-05-01 | 32 | 20
|  | 246 | 194 | MWs
Crystal River 1 | 2024-12-01 | 376 | 375
Crystal River 2 | 2024-12-01 | 498 | 492
|  | 874 | 867 | MWs
No POD Deration modeled for the Cases with No Cooling Tower
Must Run Units (Minimum Segment Only)
Crystal River 3 | All the time
Suwannee 1-3 | Summer Only
Bartow 4x1 CC | All the time
Extended Renewables and Cogens | Capacity MW
Pinellas | 54.8 | Renewables
Lake County | 12.8 | Renewables
Pasco County | 23 | Renewables
Dade County | 43 | Renewables
Ridge Generation | 39.6 | Renewables
173.2
Cogens that Expire during the Planning Period | Capacity MW |  | Expiration Date
Orange | 74 | Cogen | 2025-12-01
Orlando | 79.2 | Cogen | 2023-12-01
Mulberry | 115 | Cogen | 2024-08-01
Lake Cogen | 110 | Cogen | 2013-07-01
El Dorado | 114.2 | Cogen | 2013-12-01
LFC | 17 | Cogen | 2013-12-01
509.4
Fuel Burned
Anclote 1 and 2 | Each unit burns up to 200 MWs of Gas, the rest is Oil
Suwannee Peakers 1-3 | Oil and Gas | (Peaker # 2 used to burn Oil only)-Email from Dana Baumann
Load | Files |  |  | Provided by | On
REG | x_SF_201001_TYSP_r_20110110.xlsx |  |  | Ed Lynch | 2011-01-10
| x_MW_201001_TYSP_r_20110110.xlsx |  |  | Ed Lynch | 2011-01-10
Fuel Forecast
Natural Gas | FL Natural Gas Spot and Hedge Forecast 2010_1014.xlsx |  |  | Elaine Parker | 2010-10-14
Oil #6 | FL Num 6 Oil Costs Spot and Hedge 2010_1019.xlsx |  |  | Elaine Parker | 2010-10-19
Oil #2 | FL Num 2 Oil Costs Spot and Hedge 2010_1014.xlsx |  |  | Elaine Parker | 2010-10-14
Coal - Average Fuel Prices | FL_Coal Costs_2010_1118_updated burn.xlsx |  |  | Daphne Ingram | 2010-11-18
Nuclear | FL Nuclear Costs 2010_1015.xlsx |  |  | Ken Nelson | 2010-10-14
|  | Gross MW Output | Capital $M
Alternatives | In Service Date |  | 2011 | 2012 | 1905-07-05
CR3_EPU Best Case | 2013-01-03 | 1080 | 89 | 147 | 13.5
CR3_EPU Most Probable Case | 2013-04-30 | 1080 | 89 | 147 | 15
CR3_EPU Worst Case | 2013-10-30 | 1080 | 89 | 147 | 18
CR3_EPU Cancellation - With LPT Only | 2013-01-03 | 940 | 34.8 | 13.6
CR3_EPU Cancellation - No LPT No HPT | 2013-01-03 | 916 | 34.8 | 8.6
CR3_EPU Cancellation - LPT and HPT | 2013-01-03 | 912 | 34.8 | 16.5
Cooling Tower | 2013-06-01
No Cooling Tower | 2011-06-01
The first 3 projects go along with the Cooling Tower Project
The 3 cancellation projects go along with the No Cooling Tower Project |  |  | Strategist
Alternatives | Winter MW | Summer MW | OVERNIGHT COSTS $2010 | First Year Available | Last Year Available
Combustion Turbine - Brownfield | 205 | 178 | 98389 | 2017 | 2036
Combined Cycle 2x1 G - Greenfield | 875 | 767 | 787305 | 2017 | 2036
Combined Cycle 2x1 G - Brownfield | 875 | 767 | 805875 | 2017 | 2036
Levy 1 at 100% | 1120 | 1092 | 8131715 | 2021 | 2021
Levy 2 at 100% | 1120 | 1092 | 4466189 | 2022 | 2022
No Transmission Costs assigned to the Combustion Turbine

## CAPACITY_TRANS (hidden)
SEASONS | Data Item | TRANSACTION | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| CAPABILITY ADJUSTMENT |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | AS AV-RN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | PINELLAS | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | AS AV-CG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | LFC | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | LAKECNTY | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | PASCOCTY | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | DADE CTY | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | LKECOGEN | 110 | 110 | 110 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | ORLANDO | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | ELDORADO | 114.2 | 114.2 | 114.2 | 114.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | MULBERRY | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | RIDGEGEN | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | ORANGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | BIOM EG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | BG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | BG&E2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | Horizon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | Vision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | SUWBIOM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | SEASONAL TRANSACTION FIRM CAPACITY | CAP PURC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | AS AV-RN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | PINELLAS | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | AS AV-CG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | LFC | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | LAKECNTY | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | PASCOCTY | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | DADE CTY | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | LKECOGEN | 110 | 110 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | ORLANDO | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | ELDORADO | 114.2 | 114.2 | 114.2 | 114.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | MULBERRY | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | RIDGEGEN | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | ORANGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | BIOM EG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | BG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | BG&E2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | Horizon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | Vision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | SUWBIOM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | SEASONAL TRANSACTION FIRM CAPACITY | CAP PURC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ENERGY_REQUIREMENTS (hidden)
Data Item | 2010: "GWH" | 2011: "GWH" | 2012: "GWH" | 2013: "GWH" | 2014: "GWH" | 2015: "GWH" | 2016: "GWH" | 2017: "GWH" | 2018: "GWH" | 2019: "GWH" | 2020: "GWH" | 2021: "GWH" | 2022: "GWH" | 2023: "GWH" | 2024: "GWH" | 2025: "GWH" | 2026: "GWH" | 2027: "GWH" | 2028: "GWH" | 2029: "GWH" | 2030: "GWH" | 2031: "GWH" | 2032: "GWH" | 2033: "GWH" | 2034: "GWH" | 2035: "GWH" | 2036: "GWH" | 2037: "GWH" | 2038: "GWH"
ENERGY REQUIREMENTS | 43818.5586 | 42750.1797 | 44442.6328 | 45876.6797 | 46458.0078 | 46815.2734 | 46477.2773 | 46342.625 | 46932.3945 | 47921.6367 | 48871.1133 | 49462.7383 | 50024.7734 | 49657.875 | 50296.957 | 50794.3164 | 51468.0938 | 52151.8594 | 52843.4102 | 53533.4766 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609 | 54200.9609

## CAPACITY_DET (hidden)
SEASONS | Unit Type | THERMAL UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
JANUARY |  | ANC1ENV 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | ANC2ENV 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | NucTran1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | NucTran2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | RLR1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | RLR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | CAPX-P1A 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | CAPX-P2A 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | CAPX-P1B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | CAPX-P2B 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | CAPX-P2A 795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120
JANUARY |  | CAPX-P1A 797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120 | 1120
JANUARY |  | NucTran2 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY |  | NucTran1 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | HINESW 1 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528 | 528
JANUARY | CC | HINESW 2 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563 | 563
JANUARY | CC | TIGERBAY 1 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224
JANUARY | CC | HINES 3 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564 | 564
JANUARY | CC | HINES 4 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544 | 544
JANUARY | CC | Bar(4X1) 1 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171 | 1171
JANUARY | CC | HINESS 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | HINESS 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | ANC1RPW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | ANC2RPW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | SUWRPWR 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1FP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1FP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1FS1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1FS2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC3x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC3x1GP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC4x1FP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC4x1FP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1GFP 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC2x1GFP 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC1x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CC | CC1x1GP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | UF 1 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
JANUARY | CT | PAVON PK 1 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PAVON PK 2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PBARTOW 1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
JANUARY | CT | PBARTOW 2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
JANUARY | CT | PBARTOW 3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
JANUARY | CT | PBARTOW 4 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
JANUARY | CT | PBAYBORO 1 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
JANUARY | CT | PBAYBORO 2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
JANUARY | CT | PBAYBORO 3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
JANUARY | CT | PBAYBORO 4 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
JANUARY | CT | DEBARY 1 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
JANUARY | CT | DEBARY 2 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
JANUARY | CT | DEBARY 3 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
JANUARY | CT | DEBARY 4 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
JANUARY | CT | DEBARY 5 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
JANUARY | CT | DEBARY 6 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
JANUARY | CT | DEBARY 7 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
JANUARY | CT | DEBARY 8 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
JANUARY | CT | DEBARY 9 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97
JANUARY | CT | DEBARY 10 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97
JANUARY | CT | PHIGGINS 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PHIGGINS 2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PHIGGINS 3 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PHIGGINS 4 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | INT CITY 1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
JANUARY | CT | INT CITY 2 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
JANUARY | CT | INT CITY 3 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
JANUARY | CT | INT CITY 4 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
JANUARY | CT | INT CITY 5 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
JANUARY | CT | INT CITY 6 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
JANUARY | CT | INT CITY 7 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94
JANUARY | CT | INT CITY 8 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
JANUARY | CT | INT CITY 9 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
JANUARY | CT | INT CITY 10 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
JANUARY | CT | INT CITY 11 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
JANUARY | CT | INT CITY 12 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
JANUARY | CT | INT CITY 13 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94
JANUARY | CT | INT CITY 14 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
JANUARY | CT | PINAR 1 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | P SWAN 1 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
JANUARY | CT | P SWAN 2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
JANUARY | CT | P SWAN 3 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
JANUARY | CT | PTURNER 1 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PTURNER 2 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | PTURNER 3 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
JANUARY | CT | PTURNER 4 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
JANUARY | CT | AGT P1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | AGT P2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | AGT P1 B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | AGT P2 B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | CT | AGT P1 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.3 | 205.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | ANCLOTWA 1 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206
JANUARY | FOSSIL | ANCLOTC 2 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
JANUARY | FOSSIL | CRYSTAL 1 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | CRYSTAL 2 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | CRYSTAL 4 | 732 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712 | 712
JANUARY | FOSSIL | CRYSTAL 5 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 709
JANUARY | FOSSIL | SUWANNEW 1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | SUWANNEW 2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | SUWANNEW 3 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | ANCLOTSA 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | SUWANNES 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | SUWANNES 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | SUWANNES 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | ANCLOTWB 1 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311
JANUARY | FOSSIL | ANCLOTSB 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | FOSSIL | ANCLOTD 2 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331 | 331
JANUARY | NUCLEAR | CR NUC 3 | 805.086 | 809.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31
JANUARY | NUCLEAR | ALWR-P 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | NUCLEAR | ALWR-P 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | NUCLEAR | ALWR-P 794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | NUCLEAR | ALWR-P 796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | MILL UPS 1 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | TECO 1 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | Franklin 1 | 0 | 341 | 341 | 341 | 341 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | Scherer 1 | 0 | 71 | 71 | 71 | 71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VANDREL 1 | 0 | 159.58 | 159.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VANDREL 2 | 0 | 0 | 159.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | FRNKEXT 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | OSCREL 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VandoNSG 1 | 0 | 0 | 0 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VandoNSG 2 | 0 | 0 | 0 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VandoNSG 3 | 0 | 0 | 0 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | VandoNSG 4 | 0 | 0 | 0 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 166.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | ShadyHls 1 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | ShadyHls 2 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | PPA | ShadyHls 3 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 173.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | TRANSM | ANC1TRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | TRANSM | ANC2TRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | TRANSM | SUWTRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | ANC1ENV 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | ANC2ENV 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | NucTran1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | NucTran2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | RLR1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | RLR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | CAPX-P1A 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | CAPX-P2A 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | CAPX-P1B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | CAPX-P2B 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | CAPX-P2A 795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106
AUGUST |  | CAPX-P1A 797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106 | 1106
AUGUST |  | NucTran2 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | NucTran1 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | HINESW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | HINESW 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | TIGERBAY 1 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
AUGUST | CC | HINES 3 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488 | 488
AUGUST | CC | HINES 4 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472 | 472
AUGUST | CC | Bar(4X1) 1 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133
AUGUST | CC | HINESS 1 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462
AUGUST | CC | HINESS 2 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490
AUGUST | CC | ANC1RPW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | ANC2RPW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | SUWRPWR 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1FP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1FP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1FS1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1FS2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC3x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC3x1GP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC4x1FP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC4x1FP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1GFP 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC2x1GFP 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC1x1GP1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CC | CC1x1GP2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | UF 1 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999 | 45.999
AUGUST | CT | PAVON PK 1 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PAVON PK 2 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PBARTOW 1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
AUGUST | CT | PBARTOW 2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
AUGUST | CT | PBARTOW 3 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
AUGUST | CT | PBARTOW 4 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
AUGUST | CT | PBAYBORO 1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
AUGUST | CT | PBAYBORO 2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
AUGUST | CT | PBAYBORO 3 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
AUGUST | CT | PBAYBORO 4 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
AUGUST | CT | DEBARY 1 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
AUGUST | CT | DEBARY 2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
AUGUST | CT | DEBARY 3 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
AUGUST | CT | DEBARY 4 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
AUGUST | CT | DEBARY 5 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
AUGUST | CT | DEBARY 6 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
AUGUST | CT | DEBARY 7 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
AUGUST | CT | DEBARY 8 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
AUGUST | CT | DEBARY 9 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
AUGUST | CT | DEBARY 10 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
AUGUST | CT | PHIGGINS 1 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PHIGGINS 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PHIGGINS 3 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PHIGGINS 4 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | INT CITY 1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
AUGUST | CT | INT CITY 2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
AUGUST | CT | INT CITY 3 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
AUGUST | CT | INT CITY 4 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
AUGUST | CT | INT CITY 5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
AUGUST | CT | INT CITY 6 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
AUGUST | CT | INT CITY 7 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
AUGUST | CT | INT CITY 8 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
AUGUST | CT | INT CITY 9 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
AUGUST | CT | INT CITY 10 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
AUGUST | CT | INT CITY 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | INT CITY 12 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
AUGUST | CT | INT CITY 13 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
AUGUST | CT | INT CITY 14 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
AUGUST | CT | PINAR 1 | 11.999 | 11.999 | 11.999 | 11.999 | 11.999 | 11.999 | 11.999 | 11.999 | 11.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | P SWAN 1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
AUGUST | CT | P SWAN 2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
AUGUST | CT | P SWAN 3 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
AUGUST | CT | PTURNER 1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PTURNER 2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | PTURNER 3 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
AUGUST | CT | PTURNER 4 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
AUGUST | CT | AGT P1 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | AGT P2 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | AGT P1 B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | AGT P2 B 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | CT | AGT P1 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177.51 | 177.51 | 177.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | ANCLOTWA 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | ANCLOTC 2 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
AUGUST | FOSSIL | CRYSTAL 1 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 374.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | CRYSTAL 2 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | CRYSTAL 4 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699
AUGUST | FOSSIL | CRYSTAL 5 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699 | 699
AUGUST | FOSSIL | SUWANNEW 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | SUWANNEW 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | SUWANNEW 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | ANCLOTSA 1 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
AUGUST | FOSSIL | SUWANNES 1 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | SUWANNES 2 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | SUWANNES 3 | 71 | 71 | 71 | 71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | ANCLOTWB 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | FOSSIL | ANCLOTSB 1 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301
AUGUST | FOSSIL | ANCLOTD 2 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
AUGUST | NUCLEAR | CR NUC 3 | 793.476 | 793.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7
AUGUST | NUCLEAR | ALWR-P 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | NUCLEAR | ALWR-P 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | NUCLEAR | ALWR-P 794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | NUCLEAR | ALWR-P 796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 1092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | MILL UPS 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | TECO 1 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | Franklin 1 | 341 | 341 | 341 | 341 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | Scherer 1 | 71 | 71 | 71 | 71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VANDREL 1 | 154.05 | 154.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VANDREL 2 | 0 | 154.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | FRNKEXT 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | OSCREL 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VandoNSG 1 | 0 | 0 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VandoNSG 2 | 0 | 0 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VandoNSG 3 | 0 | 0 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | VandoNSG 4 | 0 | 0 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 156.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | ShadyHls 1 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | ShadyHls 2 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | PPA | ShadyHls 3 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 159.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | TRANSM | ANC1TRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | TRANSM | ANC2TRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | TRANSM | SUWTRN 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## CAPACITY (hidden)
SEASONS | Unit Type | 2010: "MW" | 2011: "MW" | 2012: "MW" | 2013: "MW" | 2014: "MW" | 2015: "MW" | 2016: "MW" | 2017: "MW" | 2018: "MW" | 2019: "MW" | 2020: "MW" | 2021: "MW" | 2022: "MW" | 2023: "MW" | 2024: "MW" | 2025: "MW" | 2026: "MW" | 2027: "MW" | 2028: "MW" | 2029: "MW" | 2030: "MW" | 2031: "MW" | 2032: "MW" | 2033: "MW" | 2034: "MW" | 2035: "MW" | 2036: "MW" | 2037: "MW" | 2038: "MW"
JANUARY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240
JANUARY | CC | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594 | 3594
JANUARY | CT | 3092 | 3092 | 3092 | 3092 | 3092 | 3092 | 3092 | 3092 | 3092 | 3297.3 | 3051.3 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846 | 2846
JANUARY | FOSSIL | 3500 | 3480 | 3480 | 3480 | 3480 | 3480 | 3480 | 3347 | 3347 | 3347 | 3347 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473 | 2473
JANUARY | NUCLEAR | 805.086 | 809.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 2080.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 960.086 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31 | 959.31
JANUARY | PPA | 1004.953 | 1162.533 | 1252.113 | 1600.1114 | 1600.1114 | 1600.1114 | 1600.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 1188.1114 | 667.1584 | 667.1584 | 667.1584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JANUARY | TRANSM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212
AUGUST | CC | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250 | 3250
AUGUST | CT | 2346.998 | 2346.998 | 2346.998 | 2346.998 | 2346.998 | 2346.998 | 2346.998 | 2346.998 | 2524.508 | 2330.509 | 2330.509 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999 | 2152.999
AUGUST | FOSSIL | 3408.999 | 3408.999 | 3408.999 | 3408.999 | 3408.999 | 3408.999 | 3277.999 | 3277.999 | 3277.999 | 3277.999 | 3277.999 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409 | 2409
AUGUST | NUCLEAR | 793.476 | 793.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 2036.476 | 2036.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 944.476 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7 | 943.7
AUGUST | PPA | 1115.534 | 1199.584 | 1516.404 | 1516.404 | 1516.404 | 1516.404 | 1104.404 | 1104.404 | 1104.404 | 1104.404 | 1104.404 | 1104.404 | 1104.404 | 1104.404 | 624.92 | 624.92 | 624.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUGUST | TRANSM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SYSTEM_VALUES (hidden)
Data Item | SEASONS | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
PEAK DEMAND | JANUARY | 9753.415 | 9608.415 | 9870.415 | 10050.415 | 9620.415 | 9693.415 | 9746.415 | 9883.416 | 9996.416 | 10133.417 | 10524.4131 | 10672.4121 | 10825.4141 | 10686.4121 | 10845.4111 | 11012.4111 | 11176.4131 | 11345.415 | 11513.417 | 11683.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111 | 11854.4111
PEAK DEMAND | AUGUST | 9037.415 | 8842.415 | 9041.415 | 9126.415 | 8987.415 | 9052.415 | 9195.415 | 9274.415 | 9383.415 | 9763.415 | 9899.415 | 10042.415 | 10192.4189 | 10047.415 | 10207.4131 | 10371.418 | 10535.4199 | 10703.418 | 10871.418 | 11042.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418 | 11214.418
INSTALLED CAPACITY | JANUARY | 12678.6396 | 12820.2197 | 13060.7998 | 13408.7998 | 13167.5996 | 13167.5996 | 13167.5996 | 12622.5996 | 12622.5996 | 12827.8994 | 13701.8994 | 13742.5996 | 13742.5996 | 13742.5996 | 13663.3994 | 13027.4453 | 13027.4453 | 13027.4453 | 12360.2852 | 12360.2852 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098 | 12359.5098
INSTALLED CAPACITY | AUGUST | 11597.6064 | 11681.6562 | 12149.4785 | 12039.4785 | 11908.2783 | 11908.2783 | 11365.2783 | 11365.2783 | 11542.7881 | 12440.79 | 12440.79 | 12514.2803 | 12514.2803 | 12514.2803 | 11955.5957 | 11840.5957 | 11840.5957 | 11215.6738 | 11215.6738 | 11215.6738 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984 | 11214.8984
RESERVE MARGIN PERCENT | JANUARY | 29.9918 | 33.427 | 32.3227 | 33.4154 | 36.8714 | 35.8407 | 35.102 | 27.7149 | 26.2713 | 26.5901 | 30.1916 | 28.7675 | 26.9476 | 28.5988 | 25.9832 | 18.2978 | 16.562 | 14.8256 | 7.3555 | 5.7935 | 4.2608 | 4.2608 | 4.2608 | 4.2608 | 4.2608 | 4.2608 | 4.2608 | 4.2608 | 4.2608
RESERVE MARGIN PERCENT | AUGUST | 28.3288 | 32.1093 | 34.3759 | 31.919 | 32.4995 | 31.5481 | 23.5972 | 22.5444 | 23.0127 | 27.4225 | 25.672 | 24.6143 | 22.7803 | 24.5522 | 17.1266 | 14.1656 | 12.3885 | 4.7859 | 3.1666 | 1.569 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844

## Peakers_Retirement (hidden)
| Seasonal Thermal Firm Capacity | SEASONS | SEASONS
|  | 2018 | 2019
| (MW) | AUGUST | AUGUST
18 | PAVON PK 1 | 24 | 0 | -24
19 | PAVON PK 2 | 24 | 0 | -24
38 | PHIGGINS 1 | 26 | 0 | -26
39 | PHIGGINS 2 | 25 | 0 | -25
40 | PHIGGINS 3 | 33 | 0 | -33
41 | PHIGGINS 4 | 30 | 0 | -30
56 | PINAR 1 | 11.999 | 0 | -11.999
60 | PTURNER 1 | 10 | 0 | -10
61 | PTURNER 2 | 10 | 0 | -10
-193.999