## Cypress Lakes
248/095 - Cypress Lakes - 2019
| Operating Permit No.: | FLA013123 |  |  |  | Expires: | 2019-04-29
| Plant Permitted Capacity: | 0.190 mgd AADF | [9 empty] | From Historical Data
| Perc Ponds/Surf Discharge: | N/A | [9 empty] | From Daily Flow Worksheet
| Reuse/Public Access: | 0.175 mgd | [9 empty] | Manual data entry from DMR
Hyperlinks!A1
| Flow FLW-1 (Cypress Lakes Golf Course) |  |  | CBOD5 |  |  | TSS | pH |  | Fecal Coliform | Fecal Coliform | Turbidity | TRC | CBOD | TSS
| An Avg | Mo Avg | Peak | An Avg | Mo Avg | Max | Max | Min | Max | 75% Min | Max | Max | Min | INF | INF
| mgd | mgd | mgd | mg/L | mg/L | mg/L | mg/L | SU | SU |  | #/100ml | NTU | mg/L | mg/L | mg/L
Limit | 0.175 |  |  | 20 | 30 | 60 | 5 | 6 | 8.5 | NonDetec | 25 |  | 1 | Report | Report
2019-01-01 | 0.11854 | 0.12005 | 0.15943 | 3.53 | 5.7 | 12 | 3.2 | 7.2 | 7.6 | 100% | 1 | 2.2 | 1 | 250 | 400
February | 0.12432 | 0.13186 | 0.15425 | 3.51 | 2.8 | 3.4 | 1.6 | 7.2 | 7.6 | 100% | 1 | 2.5 | 1 | 220 | 260
March | 0.12197 | 0.12881 | 0.14885 | 3.55 | 3.05 | 3.2 | 1.6 | 7.2 | 7.6 | 100% | 1 | 2.5 | 1 | 260 | 370
April | 0.11213 | 0.11559 | 0.13825 | 3.54 | 2.4 | 2.4 | 2.6 | 7.2 | 7.6 | 83.4% | 104 | 2 | 1 | 200 | 360
May | 0.102 | 0.094586 | 0.11985 | 3.38 | 4.4 | 5 | 1 | 7.2 | 7.5 | 100% | 1 | 4.3 | 1.1 | 210 | 230
June | 0.095 | 0.096225 | 0.11593 | 3.47 | 3 | 3 | 1.6 | 7.2 | 7.5 | 100% | 1 | 4.5 | 1.2 | 160 | 190
July | 0.1 | 0.10642 | 0.1491 | 3.37 | 2.17 | 2.5 | 2 | 7.2 | 7.8 | 94% | 36 | 4.5 | 1.1 | 250 | 330
August | 0.096 | 0.10207 | 0.11736 | 3.39 | 3 | 3.6 | 1.6 | 7.3 | 7.8 | 100% | 1 | 3.6 | 1.4 | 200 | 270
September | 0.094558 | 0.093252 | 0.11276 | 3.4 | 2.05 | 2.1 | 1 | 7.2 | 7.7 | 94.5% | 2 | 3.2 | 1 | 190 | 240
October | 0.097186 | 0.10599 | 0.16352 | 3.36 | 2.2 | 2.4 | 2 | 27.2 | 7.8 | 94.8% | 3 | 3.5 | 1 | 190 | 390
November | 0.109 | 0.10815 | 0.15506 | 3.38 | 4.5 | 6 | 3.2 | 7.3 | 7.8 | 100% | 1 | 2.6 | 1.2 | 300 | 400
December | 0.11264 | 0.1146 | 0.19203 | 3.12 | 2.4 | 2.8 | 2 | 7.3 | 7.9 | 89% | 6 | 2 | 2.6 | 340 | 390
Average | 0.10589 | 0.10887 | 0.14245 | 3.4064 | 2.9064 | 3.3091 | 1.8364 | 9.0455 | 7.6909 | 0.95973 | 14.2727 | 3.2 | 1.2364 | 229.0909 | 311.8182
Minimum | 0.094558 | 0.093252 | 0.11276 | 3.12 | 2.05 | 2.1 | 1 | 7.2 | 7.5 | 0.834 | 1 | 2 | 1 | 160 | 190
Maximum | 0.12432 | 0.13186 | 0.19203 | 3.55 | 5.7 | 12 | 3.2 | 27.2 | 7.9 | 1 | 104 | 4.5 | 2.6 | 340 | 400
Historical Data
| REUSE MOAVG | CBOD MOAVG
R12MOAVG |  |  | Change formula before entering the next month's data
2018-01-01 | 0.11854 | 4.6 | Jacquee
February | 0.12432 | 3.05 | 1 | Copy/Paste Value' the 2018 Historical Data from the 2018 DMR Summaries workbook.
March | 0.12197 | 2.65 | 2 | Enter in the formulas/links into the 2019 Table below and also the formulas in row 36
April | 0.11213 | 2.3
May | 0.102 | 6.25 | 10/24/2019 Email:
June | 0.095 | 2
July | 0.1 | 3.3
August | 0.096 | 2.77
September | 0.094558 | 2
October | 0.097186 | 2.6
November | 0.109 | 4.35
December | 0.11264 | 5.5
2019-01-01 | 0.12005 | 5.7
February | 0.13186 | 2.8
March | 0.12881 | 3.05
April | 0.11559 | 2.4
May | 0.094586 | 4.4
June | 0.096225 | 3
July | 0.10642 | 2.17
August | 0.10207 | 3
September | 0.093252 | 2.05
October | 0.10599 | 2.2
November | 0.10815 | 4.5
December | 0.1146 | 2.4
Note on E9: From page 1 of DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082 EFA-01'
Note on H9: From page 1 of DMR 'Solids, Total Suspended PARM Code 00530 EFB-01'
Note on I9: From page 2 of DMR pH PARM Code 00406 EFA-01'
Note on K9: From page 2 of DMR 'Coliform, Fecal % less than detection PARM Code 51005 EFA-01'
Note on L9: From page 2 of DMR 'Coliform, Fecal PARM Code 74055 EFA-01'
Note on L16: Jacquee Chandler: Sample failed due to sampling error cl2 a little lower than normal just above low limit.
Note on L19: Jacquee Chandler: 07-01 Fecal was 36 but on 07-02 it was back down to 1. possible bad sample.
Note on H24: Jacquee Chandler: Continually monitoring TSS not Turbidity.

## Cypress Lakes Flow Summary
2019 Cypress Lakes - DMR Flow Summary | [5 empty] | Hyperlinks!A1
Note: Steve Fuller will provide the DMR Part B in Excel form. Copy/Paste Special-Value-Transpose.
FLW-01
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0.13268 | 0.141 | 0.13296 | 0.12812 | 0.13311 | 0.11601 | 0.11793 | 0.11747 | 0.12304 | 0.11739 | 0.11201 | 0.1197 | 0.097256 | 0.10019 | 0.14837 | 0.14131 | 0.12424 | 0.098291 | 0.13071 | 0.12054 | 0.064765 | 0.15218 | 0.14008 | 0.15943 | 0.10096 | 0.11884 | 0.078316 | 0.07791 | 0.11959 | 0.13035 | 0.1269 | 3.7216 | 0.12005 | 0.15943
February | 0.13263 | 0.15292 | 0.15425 | 0.11216 | 0.11721 | 0.13458 | 0.12519 | 0.11179 | 0.12795 | 0.15232 | 0.1146 | 0.14892 | 0.14194 | 0.11012 | 0.12079 | 0.1371 | 0.13648 | 0.14234 | 0.13331 | 0.12567 | 0.1369 | 0.12864 | 0.14133 | 0.13393 | 0.12222 | 0.13705 | 0.12833 | 0.13149 |  |  |  | 3.6922 | 0.13186 | 0.15425
March | 0.11855 | 0.1339 | 0.13491 | 0.13121 | 0.13494 | 0.1153 | 0.12004 | 0.11664 | 0.13132 | 0.13031 | 0.1421 | 0.12502 | 0.13106 | 0.12579 | 0.12604 | 0.13391 | 0.14018 | 0.12687 | 0.14526 | 0.13561 | 0.12857 | 0.12112 | 0.11559 | 0.11227 | 0.14885 | 0.12375 | 0.14194 | 0.12666 | 0.12295 | 0.11669 | 0.13563 | 3.993 | 0.12881 | 0.14885
April | 0.13238 | 0.12866 | 0.11799 | 0.12823 | 0.13392 | 0.13146 | 0.12333 | 0.1253 | 0.11902 | 0.10774 | 0.1176 | 0.098493 | 0.13825 | 0.1276 | 0.13195 | 0.096347 | 0.10122 | 0.11982 | 0.12016 | 0.12244 | 0.10359 | 0.11371 | 0.098779 | 0.10606 | 0.10454 | 0.10048 | 0.11089 | 0.1025 | 0.10399 | 0.10139 |  | 3.4678 | 0.11559 | 0.13825
May | 0.096813 | 0.10544 | 0.087072 | 0.10713 | 0.11985 | 0.11032 | 0.084176 | 0.093575 | 0.11708 | 0.091327 | 0.10487 | 0.095311 | 0.1076 | 0.11666 | 0.095612 | 0.084834 | 0.077676 | 0.10029 | 0.084155 | 0.081505 | 0.09531 | 0.087582 | 0.091156 | 0.078764 | 0.098159 | 0.097543 | 0.073993 | 0.098942 | 0.08461 | 0.088311 | 0.076494 | 2.9322 | 0.094586 | 0.11985
June | 0.10649 | 0.10001 | 0.10698 | 0.088051 | 0.10933 | 0.08752 | 0.077582 | 0.10869 | 0.092667 | 0.084828 | 0.096978 | 0.098631 | 0.11277 | 0.077551 | 0.11593 | 0.10292 | 0.092244 | 0.10433 | 0.097132 | 0.097804 | 0.07981 | 0.10034 | 0.09768 | 0.093828 | 0.089699 | 0.084446 | 0.092968 | 0.099621 | 0.099543 | 0.090385 |  | 2.8868 | 0.096225 | 0.11593
July | 0.099108 | 0.11008 | 0.093772 | 0.1491 | 0.07573 | 0.11724 | 0.13766 | 0.11292 | 0.10913 | 0.11455 | 0.10029 | 0.10025 | 0.10988 | 0.096199 | 0.096319 | 0.099277 | 0.096598 | 0.11567 | 0.083168 | 0.11581 | 0.1077 | 0.12302 | 0.091751 | 0.11066 | 0.13117 | 0.091746 | 0.10838 | 0.094492 | 0.094158 | 0.091976 | 0.12118 | 3.299 | 0.10642 | 0.1491
August | 0.11314 | 0.09915 | 0.11446 | 0.090102 | 0.10131 | 0.10012 | 0.094863 | 0.11736 | 0.11139 | 0.11565 | 0.10182 | 0.11215 | 0.097743 | 0.11175 | 0.09944 | 0.10701 | 0.1068 | 0.099999 | 0.094174 | 0.081876 | 0.086748 | 0.10249 | 0.077292 | 0.11281 | 0.094606 | 0.097452 | 0.10898 | 0.10305 | 0.099892 | 0.097623 | 0.11306 | 3.1643 | 0.10207 | 0.11736
September | 0.10691 | 0.11276 | 0.10252 | 0.096582 | 0.094869 | 0.085156 | 0.091862 | 0.088895 | 0.087241 | 0.090951 | 0.086242 | 0.10017 | 0.085152 | 0.10725 | 0.10792 | 0.10739 | 0.081824 | 0.087712 | 0.084472 | 0.095796 | 0.096452 | 0.085918 | 0.091563 | 0.083381 | 0.085221 | 0.086285 | 0.079497 | 0.098544 | 0.096624 | 0.092398 |  | 2.7976 | 0.093252 | 0.11276
October | 0.07179 | 0.086081 | 0.090384 | 0.10441 | 0.094254 | 0.092021 | 0.092493 | 0.12273 | 0.10365 | 0.10484 | 0.10266 | 0.089007 | 0.10054 | 0.10729 | 0.085994 | 0.10295 | 0.10804 | 0.11389 | 0.16352 | 0.13262 | 0.11644 | 0.10168 | 0.092666 | 0.11348 | 0.10304 | 0.1377 | 0.12502 | 0.10119 | 0.10591 | 0.11022 | 0.10912 | 3.2856 | 0.10599 | 0.16352
November | 0.086959 | 0.15187 | 0.081567 | 0.10537 | 0.11527 | 0.11111 | 0.12045 | 0.12381 | 0.10012 | 0.1038 | 0.10448 | 0.1105 | 0.066732 | 0.11058 | 0.15506 | 0.11242 | 0.12984 | 0.10218 | 0.098205 | 0.10356 | 0.094152 | 0.091357 | 0.12146 | 0.10845 | 0.14834 | 0.00872 | 0.1264 | 0.1447 | 0.10035 | 0.10658 |  | 3.2444 | 0.10815 | 0.15506
December | 0.11686 | 0.10397 | 0.10019 | 0.097825 | 0.10139 | 0.085339 | 0.19203 | 0.030221 | 0.10597 | 0.11663 | 0.09609 | 0.1232 | 0.10105 | 0.10486 | 0.11651 | 0.10793 | 0.13199 | 0.11207 | 0.10832 | 0.094169 | 0.10102 | 0.12509 | 0.13933 | 0.14706 | 0.11993 | 0.12057 | 0.12145 | 0.12939 | 0.14226 | 0.13359 | 0.12628 | 3.5526 | 0.1146 | 0.19203
| 1 | 116857 | 0.11686
| 2 | 103968 | 0.10397 | [19 empty] | 0.11314
| 3 | 100192 | 0.10019 | [19 empty] | 0.09915
| 4 | 97825 | 0.097825 | [19 empty] | 0.11446
| 5 | 101390 | 0.10139 | [19 empty] | 0.090102
| 6 | 85339 | 0.085339 | [19 empty] | 0.10131
| 7 | 192028 | 0.19203 | [19 empty] | 0.10012
| 8 | 30221 | 0.030221 | [19 empty] | 0.94886
| 9 | 105974 | 0.10597 | [19 empty] | 0.11736
| 10 | 116627 | 0.11663 | [19 empty] | 0.11139
| 11 | 96090 | 0.09609 | [19 empty] | 0.11565
| 12 | 123205 | 0.1232 | [19 empty] | 0.10182
| 13 | 101046 | 0.10105 | [19 empty] | 0.11215
| 14 | 104855 | 0.10486 | [19 empty] | 0.009743
| 15 | 116514 | 0.11651 | [19 empty] | 0.11175
| 16 | 107926 | 0.10793 | [19 empty] | 0.09944
| 17 | 131989 | 0.13199 | [19 empty] | 0.10701
| 18 | 112067 | 0.11207 | [19 empty] | 0.1068
| 19 | 108318 | 0.10832 | [19 empty] | 0.099999
| 20 | 94169 | 0.094169 | [19 empty] | 0.094174
| 21 | 101021 | 0.10102 | [19 empty] | 0.081876
| 22 | 125091 | 0.12509 | [19 empty] | 0.086748
| 23 | 139331 | 0.13933 | [19 empty] | 0.10249
| 24 | 147063 | 0.14706 | [19 empty] | 0.077292
| 25 | 119935 | 0.11993 | [19 empty] | 0.11281
| 26 | 120567 | 0.12057 | [19 empty] | 0.094606
| 27 | 121454 | 0.12145 | [19 empty] | 0.097452
| 28 | 129386 | 0.12939 | [19 empty] | 0.10898
| 29 | 142264 | 0.14226 | [19 empty] | 0.10305
| 30 | 133594 | 0.13359 | [19 empty] | 0.099892
| 31 | 126284 | 0.12628 | [19 empty] | 0.097623
|  |  | 3.5526 | [19 empty] | 0.11306
3.9303