## Lake Placid
5242/223 (641) - Lake Placid - 2019
| Operating Permit No.: | FLA014386 |  |  | Expires: | 2025-06-18
| Plant Permit Capacity: | 0.090 mgd AADF
| Perc Pond Disposal: | 0.090 mgd | [9 empty] | From Daily Flow Worksheet
Manual data entry from DMR
Hyperlinks!A1
| CBOD5 |  |  | TSS |  |  | pH |  | Fecal Coliform |  |  | TRC | Nitrate | FLW-1 | FLW-1 | FLW-1 | CBOD INF-1 | TSS INF-1
| An Avg | Mo Avg | Max | An Avg | Mo Avg | Max | Min | Max | An Avg | MoGeoMean | Max | Min | Max | AADF | Mo Avg | Peak | mg/L | mg/L
| mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | SU | SU | #/100ml | #/100ml | #/100ml | mg/L | mg/L | mgd | mgd | mgd | Report | Report
Limit | 20 | 30 | 60 | 20 | 30 | 60 | 6 | 8.5 | 200 | Report | 800 | 0.5 | 12 | 0.09 |  |  | Max | Max
2019-01-01 | 3.7 | 3.1 | 3.1 | 2.8 | 6 | 6 | 6.7 | 6.9 | 0.9 | 0.5 | <1.0 | 1.1 | 6.5 | 0.0151 | 0.516 | 0.032 | 130 | 180
February | 3.5 | 3.3 | 3.3 | 3 | 5.8 | 5.8 | 6.8 | 7.2 | 0.8 | 0.5 | <1.0 | 1.5 | 1.2 | 0.0154 | 0.5871 | 0.044 | 240 | 130
March | 3.8 | 5.2 | 5.2 | 3 | 1.6 | 1.6 | 6.8 | 7.2 | 0.8 | 0.5 | <1.0 | 1 | 2.3 | 0.0153 | 0.015387 | 0.029 | 240 | 110
April | 5.7 | 27 | 27 | 3.5 | 8.1 | 8.1 | 6.7 | 7.1 | 0.75 | 0.5 | <1.0 | 1.1 | 0.21 | 0.0156 | 0.013693 | 0.029 | 160 | 110
May | 6 | 5.5 | 5.5 | 3.5 | <0.25 | <.5 | 6.8 | 7.4 | 0.7 | 0.5 | <1.0 | 1.2 | 1.1 | 0.016 | 0.010668 | 0.019 | 55 | 11
June | 5.4 | 1 | <2.0 | 3.5 | 4.2 | 4.2 | 6.7 | 7.3 | 0.7 | 0.5 | <1.0 | 1 | <0.58 | 0.015 | 0.015367 | 0.0436 | 92 | 59
July | 5.3 | 1 | <2.0 | 3.8 | 4.4 | 4.4 | 6.9 | 7.3 | 0.9 | 4 | 4 | 1 | 9.4 | 0.015 | 0.016574 | 0.027 | 10 | 36
August | 5.4 | 3.3 | 3.3 | 3.5 | 1 | <2.0 | 6.8 | 7 | 0.9 | 1 | 1 | 1.4 | 5.6 | 0.0152 | 0.017729 | 0.0274 | 48 | 75
September | 5.7 | 9.2 | 9.2 | 3.5 | 2.2 | 2.2 | 6.7 | 6.9 | 1.6 | 9 | 9 | 1.1 | 2 | 0.0147 | 0.01023 | 0.0201 | 77 | 81
October | 5.5 | 1 | <2.0 | 3.7 | 4 | 4 | 6.6 | 7.4 | 1.6 | 1 | 1 | 0.9 | 13 | 0.014 | 0.0048355 | 0.0096 | 47 | 82
November | 5.4 | 2.3 | 2.3 | 3.4 | 1.4 | 1.4 | 6.7 | 6.9 | 1.6 | 0.5 | <1 | 2 | 2.7 | 0.014 | 0.012537 | 0.0419 | 43 | 63
December | 9.7 | 54 | 54 | 3.5 | 3.6 | 3.6 | 6.7 | 6.9 | 1.6 | 0.5 | <1 | 1.4 | 1.6 | 0.0144 | 0.016852 | 0.0485 | 470 | 190
Average | 5.5818 | 10.2545 | 13.725 | 3.4455 | 3.63 | 3.9222 | 6.7455 | 7.1455 | 1.0864 | 1.6818 | 3.75 | 1.2364 | 3.911 | 0.014964 | 0.065543 | 0.030925 | 134.7273 | 86.0909
Minimum | 3.5 | 1 | 2.3 | 2.8 | 1 | 1.4 | 6.6 | 6.9 | 0.7 | 0.5 | 1 | 0.9 | 0.21 | 0.014 | 0.0048355 | 0.0096 | 10 | 11
Maximum | 9.7 | 54 | 54 | 3.8 | 8.1 | 8.1 | 6.9 | 7.4 | 1.6 | 9 | 9 | 2 | 13 | 0.016 | 0.5871 | 0.0485 | 470 | 190
Email regarding items in RED for April 2019
Jacquee,
I have spoken with Otto. Everything looks good and everything is passing.
As far as the CBODs, They look high but 30 is the max. It could have been that the sample could have been drawn when the lift station was running verses when it is not running. Don’t really know.
As far as the nitrates, They are low but 12 is the max.
One factor that affects the results is when people leave after season and when they return. The operator will make air adjustments. Operators are constantly making adjustments when they visit the facility.
Thank you,
Lisa
Lisa Holmes
Pugh Utilities Service, Inc.
863-465-6911
Pus79@outlook.com
Note on B8: From page 1 of DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082 EFA-1'
Note on E8: From page 1 of the DMR 'Solids, Total Suspended PARM Code 00530 EFA-1'
Note on H8: From page 1 of DMR 'PH PARM Code 00400 EFA-1'
Note on M8: From page 2 of DMR 'Total Residual Chlorine (for disinfection) PARM Code 50060 EFA-1'
Note on N8: From page 2 of DMR 'Nitrogen, Nitrate, Total (as N) (If required in the permit) PARM Code 00620 ?EFA-1'
Note on R8: From page 2 of DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082 INF-1'
Note on S8: From page 2 of DMR 'Solida, Total Suspended PARM Code 00530 INF-1'
Note on J9: From page 1 of the DMR 'Coliform, Fecal PARM Code 74055 EFA-1'
Note on K9: From page 2 of the DMR 'Coliform, Fecal PARM Code 74055 EFA-1'
Note on L9: From page 2 of DMR 'Coliform, Fecal PARM Code 74055 EFA-1'
Note on N21: Jacquee Chandler: Made adjustments to plant
Note on C23: Jacquee Chandler: making adjustments to plant
Note on D23: Jacquee Chandler: making adjustments to plant

## Lake Placid Flow Summary
2019 Lake Placid DMR Flow Summary
Hyperlinks!A1
FLW-01
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0.015 | 0.019 | 0.014 | 0.0159 | 0.0149 | 0.0135 | 0.0107 | 0.017 | 0.019 | 0.014 | 0.019 | 0.016 | 0.017 | 0.018 | 0.015 | 0.016 | 0.014 | 0.013 | 0.017 | 0.018 | 0.02 | 0.016 | 0.014 | 0.009 | 0.015 | 0.012 | 0.031 | 0.032 | 0.015 | 0.018 | 0.018 | 0.516 | 0.016645 | 0.032
February | 0.026 | 0.017 | 0.022 | 0.019 | 0.015 | 0.026 | 0.019 | 0.016 | 0.018 | 0.029 | 0.03 | 0.018 | 0.02 | 0.023 | 0.017 | 0.019 | 0.016 | 0.017 | 0.017 | 0.02 | 0.019 | 0.018 | 0.02 | 0.021 | 0.018 | 0.021 | 0.044 | 0.0221 |  |  |  | 0.5871 | 0.020968 | 0.044
March | 0.021 | 0.023 | 0.015 | 0.024 | 0.023 | 0.022 | 0.024 | 0.024 | 0.029 | 0.015 | 0.015 | 0.023 | 0.014 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.011 | 0.013 | 0.013 | 0.014 | 0.016 | 0.01 | 0.01 | 0.019 | 0.011 | 0.011 | 0.009 | 0.006 | 0.012 | 0.477 | 0.015387 | 0.029
April | 0.011 | 0.029 | 0.018 | 0.013 | 0.013 | 0.005 | 0.017 | 0.022 | 0.014 | 0.0156 | 0.0121 | 0.012 | 0.0122 | 0.0165 | 0.0162 | 0.0123 | 0.012 | 0.0136 | 0.0111 | 0.0093 | 0.0169 | 0.019 | 0.011 | 0.0089 | 0.0092 | 0.0091 | 0.0069 | 0.0051 | 0.011 | 0.0288 |  | 0.4108 | 0.013693 | 0.029
May | 0.0111 | 0.0126 | 0.0184 | 0.0089 | 0.0112 | 0.01 | 0.011 | 0.0167 | 0.0128 | 0.013 | 0.0111 | 0.0133 | 0.0121 | 0.009 | 0.0091 | 0.0071 | 0.0143 | 0.0145 | 0.0058 | 0.0038 | 0.0125 | 0.0124 | 0.0045 | 0.0049 | 0.002 | 0.01 | 0.019 | 0.0131 | 0.0121 | 0.0034 | 0.011 | 0.3307 | 0.010668 | 0.019
June | 0.025 | 0.0049 | 0.0066 | 0.0111 | 0.0043 | 0.0175 | 0.0111 | 0.009 | 0.013 | 0.016 | 0.0211 | 0.013 | 0.007 | 0.0231 | 0.0167 | 0.0101 | 0.012 | 0.0167 | 0.0122 | 0.0436 | 0.0231 | 0.0133 | 0.012 | 0.0242 | 0.0123 | 0.0126 | 0.015 | 0.0267 | 0.0152 | 0.0126 |  | 0.461 | 0.015367 | 0.0436
July | 0.0111 | 0.016 | 0.0104 | 0.0101 | 0.0118 | 0.0122 | 0.025 | 0.026 | 0.0125 | 0.024 | 0.023 | 0.018 | 0.02 | 0.015 | 0.015 | 0.0149 | 0.0214 | 0.0121 | 0.0149 | 0.013 | 0.008 | 0.02 | 0.0141 | 0.013 | 0.017 | 0.019 | 0.027 | 0.016 | 0.021 | 0.017 | 0.0153 | 0.5138 | 0.016574 | 0.027
August | 0.0071 | 0.014 | 0.01 | 0.02 | 0.02 | 0.0145 | 0.0219 | 0.0167 | 0.023 | 0.0164 | 0.02 | 0.0274 | 0.0068 | 0.0006 | 0.0247 | 0.022 | 0.0241 | 0.021 | 0.023 | 0.0219 | 0.009 | 0.0178 | 0.016 | 0.0157 | 0.0204 | 0.0226 | 0.0173 | 0.0148 | 0.0175 | 0.0195 | 0.0239 | 0.5496 | 0.017729 | 0.0274
September | 0.0156 | 0.0153 | 0.0149 | 0.0201 | 0.0167 | 0.013 | 0.0134 | 0.0149 | 0.0142 | 0.014 | 0.013 | 0.0112 | 0.0183 | 0.0113 | 0.0112 | 0.013 | 0.0179 | 0.0035 | 0.0075 | 0.0028 | 0.0062 | 0.003 | 0.0041 | 0.004 | 0.004 | 0.004 | 0.005 | 0.005 | 0.004 | 0.0058 |  | 0.3069 | 0.01023 | 0.0201
October | 0.005 | 0.0042 | 0.0076 | 0.0056 | 0.0048 | 0.003 | 0.0096 | 0.0063 | 0.0056 | 0.0027 | 0.0061 | 0.0096 | 0.0035 | 0.0035 | 0.0044 | 0.0055 | 0.0035 | 0.0035 | 0.0049 | 0.0038 | 0.0053 | 0.003 | 0.0041 | 0.0046 | 0.0042 | 0.0042 | 0.0045 | 0.0047 | 0.004 | 0.004 | 0.0046 | 0.1499 | 0.0048355 | 0.0096
November | 0.0055 | 0.0034 | 0.0101 | 0.0102 | 0.0085 | 0.0106 | 0.0071 | 0.0122 | 0.0113 | 0.0193 | 0.0106 | 0.0134 | 0.006 | 0.012 | 0.0136 | 0.0114 | 0.014 | 0.0167 | 0.0133 | 0.0139 | 0.0161 | 0.007 | 0.0021 | 0.0009 | 0.0419 | 0.0148 | 0.0164 | 0.018 | 0.0179 | 0.0179 |  | 0.3761 | 0.012537 | 0.0419
December | 0.013 | 0.0133 | 0.0164 | 0.0119 | 0.0174 | 0.0107 | 0.0134 | 0.0217 | 0.0213 | 0.0064 | 0.0076 | 0.014 | 0.0217 | 0.0142 | 0.0158 | 0.0188 | 0.0176 | 0.0485 | 0.0193 | 0.0146 | 0.0151 | 0.0193 | 0.018 | 0.0202 | 0.011 | 0.0116 | 0.0179 | 0.0135 | 0.0202 | 0.0238 | 0.0142 | 0.5224 | 0.016852 | 0.0485
| 1 | 130 | 0.013
| 2 | 133 | 0.0133
| 3 | 164 | 0.0164
| 4 | 119 | 0.0119
| 5 | 174 | 0.0174
| 6 | 107 | 0.0107
| 7 | 134 | 0.0134
| 8 | 217 | 0.0217
| 9 | 213 | 0.0213
| 10 | 64 | 0.0064
| 11 | 76 | 0.0076
| 12 | 140 | 0.014
| 13 | 217 | 0.0217
| 14 | 142 | 0.0142
| 15 | 158 | 0.0158
| 16 | 188 | 0.0188
| 17 | 176 | 0.0176
| 18 | 485 | 0.0485
| 19 | 193 | 0.0193
| 20 | 146 | 0.0146
| 21 | 151 | 0.0151
| 22 | 193 | 0.0193
| 23 | 180 | 0.018
| 24 | 202 | 0.0202
| 25 | 110 | 0.011
| 26 | 116 | 0.0116
| 27 | 179 | 0.0179
| 28 | 135 | 0.0135
| 29 | 202 | 0.0202
| 30 | 238 | 0.0238
| 31 | 142 | 0.0142
|  | Total | 0.5224