## WLU
2019 | Jan Used | Jan Loss | Feb Used | Feb Loss | March Used | March Loss | April Used | April Loss | May Used | May Loss | June Used | June Loss | July Used | July Loss | Aug Used | Aug Loss | Sept Used | Sept Loss | Oct Used | Oct Loss | Nov Used | Nov Loss | Dec Used | Dec Loss | YTD Total
Cypress Lakes | 0.40259 | 0 | 0.40014 | 0 | 0.33289 | 0 | 0.46548 | 0 | 0.86234 | 0 | 1.245 | 0.0015 | 3.1295 | 0.00101 | 4.0171 | 0 | 2.2622 | 0.096 | 1.4837 | 0.055 | 1.6828 | 0.005 | 2.2822 | 0 | 18.7244
Total | 0.40259 |  | 0.40014 |  | 0.33289 |  | 0.46548 |  | 0.86234 |  | 1.2465 |  | 3.1305 |  | 4.0171 |  | 2.3582 |  | 1.5387 |  | 1.6878 |  | 2.2822

## Cypress Lakes
248/095 - Cypress Lakes
PWS ID No. 6535055
CUP No. 20013043.002 |  | Expires: 08/29/37
Permitted Annual Average Daily Withdrawal - 0.2938 mgd
Permitted Peak Monthly Withdrawal of Plant - 0.382 mgd
Water Loss-Use'!A1
Hyper Links'!A1 | [8 empty] | Source Meter Error Adj. 12/26/18
|  |  |  | Total Water Used/Loss |  |  |  |  | Well 1 12/26/18 -5.10% 05/20/19 -2.00% |  | Well 2 12/26/18 -7.40% 05/20/19 -3.00%
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Pumped, Less Gallons Loss/Used | Billed Consumption | Well 1 Meter Adj. % | Well 1 Pumped Meter Adj. Adj. | Well 2 Meter Adj. % | Well 2 Pumped Meter Adj. Adj. | Total Pumped Meter Adj. | Pumped + Source Mtr Error, Less Gals Loss/Use | Total AFW(Total Water Loss/Use + Billed) | AFW % plus source mtr. error | 2018 AFW %
January 2019 | 5.633 | 0.18171 | 0.243 | 0.40259 | 0 | 0.40259 | 5.2304 | 4.699 | -5.1% | -0.28657 | -7.4% | -0.001036 | -0.2876 | 4.9428 | 5.1015 | 95.44% | 91.41%
February | 5.732 | 0.20471 | 0.263 | 0.40014 | 0 | 0.40014 | 5.3319 | 4.4722 | -5.1% | -0.11975 | -7.4% | -0.25042 | -0.37016 | 4.9617 | 4.8724 | 90.87% | 91.63%
March | 7.211 | 0.23261 | 0.354 | 0.33289 | 0 | 0.33289 | 6.8781 | 5.4726 | -5.1% | -0.000408 | -7.4% | -0.53302 | -0.53343 | 6.3447 | 5.8055 | 86.94% | 94.01%
April | 7.326 | 0.2442 | 0.347 | 0.46548 | 0 | 0.46548 | 6.8605 | 5.0975 | -5.1% | -0.000357 | -7.4% | -0.54161 | -0.54196 | 6.3186 | 5.563 | 82% | 94.17%
May | 7.746 | 0.24987 | 0.406 | 0.86234 | 0 | 0.86234 | 6.8837 | 5.1616 | -5.1%&-2.0% | 0.00051 | -7.4%&-3.0% | -0.43496 | -0.43445 | 6.4492 | 6.024 | 82.39% | 92.06%
June | 7.602 | 0.2534 | 0.416 | 1.245 | 0.0015 | 1.2465 | 6.3555 | 4.329 | -2% | -0.00036 | -3% | -0.22752 | -0.22788 | 6.1276 | 5.5755 | 75.61% | 92.41%
July | 7.501 | 0.24197 | 0.355 | 3.1295 | 0.00101 | 3.1305 | 4.3705 | 3.7936 | -2% | -0.09872 | -3% | -0.07695 | -0.17567 | 4.1948 | 6.9241 | 94.52% | 92.65%
August | 7.68 | 0.24774 | 0.377 | 4.0171 | 0 | 4.0171 | 3.6629 | 3.4462 | -2% | -0.1533 | -3% | -0.00045 | -0.15375 | 3.5092 | 7.4633 | 99.16% | 93.96%
September | 6.575 | 0.21917 | 0.383 | 2.2622 | 0.096 | 2.3582 | 4.2168 | 4.2807 | -2% | -0.13096 | -3% | -0.00081 | -0.13177 | 4.0851 | 6.6388 | 103% | 99.07%
October | 6.51 | 0.21 | 0.31 | 1.4837 | 0.055 | 1.5387 | 4.9713 | 4.9161 | -2% | -0.12994 | -3% | -0.00039 | -0.13033 | 4.841 | 6.4548 | 101.2% | 88.49%
November | 6.817 | 0.22723 | 0.277 | 1.6828 | 0.005 | 1.6878 | 5.1292 | 5.2409 | -2% | -0.13616 | -3% | -0.00027 | -0.13643 | 4.9927 | 6.9288 | 103.7% | 90.06%
December | 7.324 | 0.23626 | 0.285 | 2.2822 | 0 | 2.2822 | 5.0419 | 5.3256 | -2% | -0.14628 | -3% | -0.0003 | -0.14658 | 4.8953 | 7.6077 | 106% | 98.92%
YTD Total/Avg/Max | 83.657 | 0.22907 | 0.416 | 18.5659 | 0.15851 | 18.7244 | 64.9326 | 56.235 |  | -1.2023 |  | -2.0677 | -3.27 | 61.6626 | 74.9594
| 83.657 | [11 empty] | -3.27 |  | 74.9594
| 0 | Proof to Daily Flow |  |  |  |  | Proof to Total Billed | 0 | [6 empty] | YTD AFW % Jan-Dec | 93.25%
Verif. W/UIWtrMn WLU wrksht & WAF Input
[5 empty] | Water Loss/Use Proof | 0
Source Meter Error Adj.
[7 empty] | AFW% Email to LN, MW | [5 empty] | Well 1 | Meter Error % | Pumped Meter Error
[7 empty] | Emailed Lee and Steve about AFW. |  |  | 2019-06-17 |  |  | 05/01-05/20/19 | 5.1% | 0.00051
[13 empty] | 05/21-05/31/19 | -2% | 0
0.00051
Source Meter Error Adj.
[13 empty] | Well 2 | Meter Error % | Pumped Meter Error
[13 empty] | 05/01-05/20/19 | -7.4% | -0.34121
[13 empty] | 05/21-05/31/19 | -3% | -0.09375
-0.43496
Note on B9: Picked up from Daily Flow. Total daily flow, Column AH
Note on C9: Picked up from Daily Flow AVG, Column AI
Note on D9: Picked up from Daily Flow MAX, Column AJ
Note on E9: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the used detail.
Note on F9: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the loss detail.
Note on Q15: Jacquee Chandler: Asked Lee about meter calib. For Well 2

## Daily Flow-095
248/095 - Cypress Lakes | [9 empty] | Hyper Links'!A1
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.193 | 0.184 | 0.202 | 0.137 | 0.13 | 0.219 | 0.221 | 0.181 | 0.187 | 0.184 | 0.157 | 0.18 | 0.229 | 0.184 | 0.189 | 0.15 | 0.243 | 0.142 | 0.174 | 0.157 | 0.209 | 0.19 | 0.185 | 0.17 | 0.171 | 0.17 | 0.179 | 0.166 | 0.176 | 0.189 | 0.185 | 5.633 | 0.18171 | 0.243 | 0
February | 0.144 | 0.169 | 0.179 | 0.222 | 0.154 | 0.236 | 0.195 | 0.169 | 0.155 | 0.171 | 0.22 | 0.17 | 0.182 | 0.227 | 0.182 | 0.188 | 0.259 | 0.234 | 0.252 | 0.234 | 0.237 | 0.185 | 0.208 | 0.222 | 0.263 | 0.201 | 0.236 | 0.238 |  |  |  | 5.732 | 0.20471 | 0.263 | 0
March | 0.172 | 0.14 | 0.354 | 0.208 | 0.233 | 0.22 | 0.225 | 0.186 | 0.135 | 0.31 | 0.289 | 0.228 | 0.238 | 0.234 | 0.198 | 0.212 | 0.258 | 0.235 | 0.208 | 0.244 | 0.235 | 0.214 | 0.202 | 0.297 | 0.268 | 0.259 | 0.226 | 0.277 | 0.21 | 0.202 | 0.294 | 7.211 | 0.23261 | 0.354 | 0
April | 0.216 | 0.304 | 0.271 | 0.231 | 0.192 | 0.211 | 0.262 | 0.288 | 0.217 | 0.272 | 0.279 | 0.199 | 0.261 | 0.169 | 0.275 | 0.253 | 0.206 | 0.222 | 0.243 | 0.21 | 0.222 | 0.305 | 0.252 | 0.252 | 0.236 | 0.184 | 0.182 | 0.307 | 0.347 | 0.258 |  | 7.326 | 0.2442 | 0.347 | 0
May | 0.257 | 0.23 | 0.209 | 0.14 | 0.31 | 0.257 | 0.227 | 0.264 | 0.199 | 0.19 | 0.18 | 0.28 | 0.242 | 0.204 | 0.224 | 0.23 | 0.196 | 0.198 | 0.269 | 0.315 | 0.249 | 0.286 | 0.265 | 0.228 | 0.261 | 0.284 | 0.406 | 0.268 | 0.283 | 0.341 | 0.254 | 7.746 | 0.24987 | 0.406 | 0
June | 0.18 | 0.416 | 0.388 | 0.269 | 0.302 | 0.26 | 0.232 | 0.21 | 0.268 | 0.274 | 0.225 | 0.26 | 0.217 | 0.212 | 0.252 | 0.23 | 0.253 | 0.19 | 0.224 | 0.192 | 0.208 | 0.202 | 0.27 | 0.321 | 0.24 | 0.309 | 0.281 | 0.217 | 0.247 | 0.253 |  | 7.602 | 0.2534 | 0.416 | 0
July | 0.288 | 0.256 | 0.264 | 0.223 | 0.317 | 0.22 | 0.279 | 0.234 | 0.231 | 0.259 | 0.188 | 0.206 | 0.156 | 0.226 | 0.247 | 0.222 | 0.22 | 0.223 | 0.168 | 0.21 | 0.317 | 0.323 | 0.222 | 0.262 | 0.252 | 0.191 | 0.355 | 0.271 | 0.194 | 0.271 | 0.206 | 7.501 | 0.24197 | 0.355 | 0
August | 0.277 | 0.184 | 0.191 | 0.288 | 0.291 | 0.244 | 0.258 | 0.256 | 0.182 | 0.114 | 0.377 | 0.285 | 0.252 | 0.227 | 0.245 | 0.209 | 0.201 | 0.283 | 0.291 | 0.193 | 0.294 | 0.288 | 0.221 | 0.292 | 0.235 | 0.321 | 0.223 | 0.283 | 0.264 | 0.223 | 0.188 | 7.68 | 0.24774 | 0.377 | 0
September | 0.298 | 0.21 | 0.276 | 0.235 | 0.247 | 0.217 | 0.193 | 0.307 | 0.297 | 0.284 | 0.277 | 0.224 | 0.221 | 0.102 | 0.164 | 0.233 | 0.175 | 0.188 | 0.16 | 0.151 | 0.157 | 0.206 | 0.159 | 0.179 | 0.204 | 0.217 | 0.204 | 0.172 | 0.235 | 0.383 |  | 6.575 | 0.21917 | 0.383 | 0
October | 0.31 | 0.252 | 0.213 | 0.188 | 0.217 | 0.209 | 0.229 | 0.173 | 0.216 | 0.175 | 0.196 | 0.15 | 0.253 | 0.245 | 0.213 | 0.236 | 0.188 | 0.164 | 0.191 | 0.217 | 0.231 | 0.208 | 0.259 | 0.203 | 0.165 | 0.203 | 0.192 | 0.206 | 0.183 | 0.241 | 0.184 | 6.51 | 0.21 | 0.31 | 0
November | 0.198 | 0.252 | 0.193 | 0.248 | 0.201 | 0.22 | 0.204 | 0.187 | 0.211 | 0.219 | 0.223 | 0.225 | 0.229 | 0.202 | 0.215 | 0.184 | 0.226 | 0.203 | 0.238 | 0.261 | 0.256 | 0.215 | 0.277 | 0.226 | 0.258 | 0.243 | 0.231 | 0.275 | 0.227 | 0.27 |  | 6.817 | 0.22723 | 0.277 | 0
December | 0.242 | 0.253 | 0.243 | 0.239 | 0.235 | 0.239 | 0.285 | 0.26 | 0.242 | 0.249 | 0.245 | 0.241 | 0.217 | 0.24 | 0.251 | 0.233 | 0.254 | 0.239 | 0.225 | 0.224 | 0.24 | 0.142 | 0.268 | 0.22 | 0.263 | 0.237 | 0.209 | 0.246 | 0.197 | 0.248 | 0.198 | 7.324 | 0.23626 | 0.285 | 0
[32 empty] | 83.657 | Grand Total

## CyprsLks Wells
Cypress Lakes Well Flows
Hyper Links'!A1
| Well 1 | Well 2
Month | 1 | 2 | Total
2019-01-01 | 5.619 | 0.014 | 5.633
February | 2.348 | 3.384 | 5.732
March | 0.008 | 7.203 | 7.211
April | 0.007 | 7.319 | 7.326
May | 0.01 | 7.736 | 7.746
June | 0.018 | 7.584 | 7.602
July | 4.936 | 2.565 | 7.501
August | 7.665 | 0.015 | 7.68
September | 6.548 | 0.027 | 6.575
October | 6.497 | 0.013 | 6.51
November | 6.808 | 0.009 | 6.817
December | 7.314 | 0.01 | 7.324
January | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Jan
| Well 1 | 0.193 | 0.184 | 0.202 | 0.137 | 0.13 | 0.219 | 0.207 | 0.181 | 0.187 | 0.184 | 0.157 | 0.18 | 0.229 | 0.184 | 0.189 | 0.15 | 0.243 | 0.142 | 0.174 | 0.157 | 0.209 | 0.19 | 0.185 | 0.17 | 0.171 | 0.17 | 0.179 | 0.166 | 0.176 | 0.189 | 0.185 | 5.619 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0
| Total | 0.193 | 0.184 | 0.202 | 0.137 | 0.13 | 0.219 | 0.221 | 0.181 | 0.187 | 0.184 | 0.157 | 0.18 | 0.229 | 0.184 | 0.189 | 0.15 | 0.243 | 0.142 | 0.174 | 0.157 | 0.209 | 0.19 | 0.185 | 0.17 | 0.171 | 0.17 | 0.179 | 0.166 | 0.176 | 0.189 | 0.185 | 5.633
February | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Feb
| Well 1 | 0.144 | 0.169 | 0.179 | 0.222 | 0.154 | 0.236 | 0.195 | 0.169 | 0.155 | 0.171 | 0.201 | 0.17 | 0.182 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.348 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 0 | 0 | 0.226 | 0.182 | 0.188 | 0.259 | 0.234 | 0.252 | 0.234 | 0.237 | 0.185 | 0.208 | 0.222 | 0.263 | 0.201 | 0.236 | 0.238 |  |  |  | 3.384 | 0
| Total | 0.144 | 0.169 | 0.179 | 0.222 | 0.154 | 0.236 | 0.195 | 0.169 | 0.155 | 0.171 | 0.22 | 0.17 | 0.182 | 0.227 | 0.182 | 0.188 | 0.259 | 0.234 | 0.252 | 0.234 | 0.237 | 0.185 | 0.208 | 0.222 | 0.263 | 0.201 | 0.236 | 0.238 |  |  |  | 5.732
March | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Mar
| Well 1 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0
| Well 2 | 0.172 | 0.14 | 0.354 | 0.208 | 0.231 | 0.22 | 0.225 | 0.186 | 0.135 | 0.31 | 0.283 | 0.228 | 0.238 | 0.234 | 0.198 | 0.212 | 0.258 | 0.235 | 0.208 | 0.244 | 0.235 | 0.214 | 0.202 | 0.297 | 0.268 | 0.259 | 0.226 | 0.277 | 0.21 | 0.202 | 0.294 | 7.203 | 0
| Total | 0.172 | 0.14 | 0.354 | 0.208 | 0.233 | 0.22 | 0.225 | 0.186 | 0.135 | 0.31 | 0.289 | 0.228 | 0.238 | 0.234 | 0.198 | 0.212 | 0.258 | 0.235 | 0.208 | 0.244 | 0.235 | 0.214 | 0.202 | 0.297 | 0.268 | 0.259 | 0.226 | 0.277 | 0.21 | 0.202 | 0.294 | 7.211
April | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | April
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.007 | 0
| Well 2 | 0.216 | 0.304 | 0.271 | 0.231 | 0.192 | 0.211 | 0.262 | 0.281 | 0.217 | 0.272 | 0.279 | 0.199 | 0.261 | 0.169 | 0.275 | 0.253 | 0.206 | 0.222 | 0.243 | 0.21 | 0.222 | 0.305 | 0.252 | 0.252 | 0.236 | 0.184 | 0.182 | 0.307 | 0.347 | 0.258 |  | 7.319 | 0
| Total | 0.216 | 0.304 | 0.271 | 0.231 | 0.192 | 0.211 | 0.262 | 0.288 | 0.217 | 0.272 | 0.279 | 0.199 | 0.261 | 0.169 | 0.275 | 0.253 | 0.206 | 0.222 | 0.243 | 0.21 | 0.222 | 0.305 | 0.252 | 0.252 | 0.236 | 0.184 | 0.182 | 0.307 | 0.347 | 0.258 | 0 | 7.326
May | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | May
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0
| Well 2 | 0.257 | 0.23 | 0.209 | 0.14 | 0.31 | 0.257 | 0.217 | 0.264 | 0.199 | 0.19 | 0.18 | 0.28 | 0.242 | 0.204 | 0.224 | 0.23 | 0.196 | 0.198 | 0.269 | 0.315 | 0.249 | 0.286 | 0.265 | 0.228 | 0.261 | 0.284 | 0.406 | 0.268 | 0.283 | 0.341 | 0.254 | 7.736 | 0
| Total | 0.257 | 0.23 | 0.209 | 0.14 | 0.31 | 0.257 | 0.227 | 0.264 | 0.199 | 0.19 | 0.18 | 0.28 | 0.242 | 0.204 | 0.224 | 0.23 | 0.196 | 0.198 | 0.269 | 0.315 | 0.249 | 0.286 | 0.265 | 0.228 | 0.261 | 0.284 | 0.406 | 0.268 | 0.283 | 0.341 | 0.254 | 7.746
June | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | June
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.018 | 0
| Well 2 | 0.18 | 0.416 | 0.388 | 0.269 | 0.302 | 0.26 | 0.232 | 0.21 | 0.268 | 0.259 | 0.222 | 0.26 | 0.217 | 0.212 | 0.252 | 0.23 | 0.253 | 0.19 | 0.224 | 0.192 | 0.208 | 0.202 | 0.27 | 0.321 | 0.24 | 0.309 | 0.281 | 0.217 | 0.247 | 0.253 |  | 7.584 | 0
| Total | 0.18 | 0.416 | 0.388 | 0.269 | 0.302 | 0.26 | 0.232 | 0.21 | 0.268 | 0.274 | 0.225 | 0.26 | 0.217 | 0.212 | 0.252 | 0.23 | 0.253 | 0.19 | 0.224 | 0.192 | 0.208 | 0.202 | 0.27 | 0.321 | 0.24 | 0.309 | 0.281 | 0.217 | 0.247 | 0.253 |  | 7.602
July | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | July
| Well 1 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.187 | 0.206 | 0.156 | 0.226 | 0.247 | 0.222 | 0.22 | 0.223 | 0.168 | 0.21 | 0.317 | 0.323 | 0.222 | 0.261 | 0.252 | 0.19 | 0.355 | 0.271 | 0.194 | 0.271 | 0.206 | 4.936 | 0
| Well 2 | 0.279 | 0.256 | 0.264 | 0.223 | 0.317 | 0.22 | 0.279 | 0.234 | 0.231 | 0.259 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2.565 | 0
| Total | 0.288 | 0.256 | 0.264 | 0.223 | 0.317 | 0.22 | 0.279 | 0.234 | 0.231 | 0.259 | 0.188 | 0.206 | 0.156 | 0.226 | 0.247 | 0.222 | 0.22 | 0.223 | 0.168 | 0.21 | 0.317 | 0.323 | 0.222 | 0.262 | 0.252 | 0.191 | 0.355 | 0.271 | 0.194 | 0.271 | 0.206 | 7.501
August | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Aug
| Well 1 | 0.277 | 0.184 | 0.191 | 0.288 | 0.277 | 0.244 | 0.258 | 0.256 | 0.182 | 0.114 | 0.377 | 0.285 | 0.251 | 0.227 | 0.245 | 0.209 | 0.201 | 0.283 | 0.291 | 0.193 | 0.294 | 0.288 | 0.221 | 0.292 | 0.235 | 0.321 | 0.223 | 0.283 | 0.264 | 0.223 | 0.188 | 7.665 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0
| Total | 0.277 | 0.184 | 0.191 | 0.288 | 0.291 | 0.244 | 0.258 | 0.256 | 0.182 | 0.114 | 0.377 | 0.285 | 0.252 | 0.227 | 0.245 | 0.209 | 0.201 | 0.283 | 0.291 | 0.193 | 0.294 | 0.288 | 0.221 | 0.292 | 0.235 | 0.321 | 0.223 | 0.283 | 0.264 | 0.223 | 0.188 | 7.68
September | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Sept
| Well 1 | 0.298 | 0.21 | 0.276 | 0.235 | 0.247 | 0.217 | 0.193 | 0.307 | 0.286 | 0.281 | 0.277 | 0.224 | 0.221 | 0.102 | 0.164 | 0.233 | 0.175 | 0.188 | 0.16 | 0.151 | 0.157 | 0.206 | 0.159 | 0.179 | 0.204 | 0.217 | 0.204 | 0.172 | 0.235 | 0.37 |  | 6.548 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 |  | 0.027 | 0
| Total | 0.298 | 0.21 | 0.276 | 0.235 | 0.247 | 0.217 | 0.193 | 0.307 | 0.297 | 0.284 | 0.277 | 0.224 | 0.221 | 0.102 | 0.164 | 0.233 | 0.175 | 0.188 | 0.16 | 0.151 | 0.157 | 0.206 | 0.159 | 0.179 | 0.204 | 0.217 | 0.204 | 0.172 | 0.235 | 0.383 |  | 6.575
October | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Oct
| Well 1 | 0.307 | 0.252 | 0.213 | 0.188 | 0.217 | 0.209 | 0.229 | 0.163 | 0.216 | 0.175 | 0.196 | 0.15 | 0.253 | 0.245 | 0.213 | 0.236 | 0.188 | 0.164 | 0.191 | 0.217 | 0.231 | 0.208 | 0.259 | 0.203 | 0.165 | 0.203 | 0.192 | 0.206 | 0.183 | 0.241 | 0.184 | 6.497 | 0
| Well 2 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0
| Total | 0.31 | 0.252 | 0.213 | 0.188 | 0.217 | 0.209 | 0.229 | 0.173 | 0.216 | 0.175 | 0.196 | 0.15 | 0.253 | 0.245 | 0.213 | 0.236 | 0.188 | 0.164 | 0.191 | 0.217 | 0.231 | 0.208 | 0.259 | 0.203 | 0.165 | 0.203 | 0.192 | 0.206 | 0.183 | 0.241 | 0.184 | 6.51
November | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Nov
| Well 1 | 0.198 | 0.252 | 0.193 | 0.248 | 0.192 | 0.22 | 0.204 | 0.187 | 0.211 | 0.219 | 0.223 | 0.225 | 0.229 | 0.202 | 0.215 | 0.184 | 0.226 | 0.203 | 0.238 | 0.261 | 0.256 | 0.215 | 0.277 | 0.226 | 0.258 | 0.243 | 0.231 | 0.275 | 0.227 | 0.27 |  | 6.808 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.009 | 0
| Total | 0.198 | 0.252 | 0.193 | 0.248 | 0.201 | 0.22 | 0.204 | 0.187 | 0.211 | 0.219 | 0.223 | 0.225 | 0.229 | 0.202 | 0.215 | 0.184 | 0.226 | 0.203 | 0.238 | 0.261 | 0.256 | 0.215 | 0.277 | 0.226 | 0.258 | 0.243 | 0.231 | 0.275 | 0.227 | 0.27 |  | 6.817
December | Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Proof | Dec
| Well 1 | 0.242 | 0.253 | 0.243 | 0.239 | 0.235 | 0.239 | 0.285 | 0.26 | 0.232 | 0.249 | 0.245 | 0.241 | 0.217 | 0.24 | 0.251 | 0.233 | 0.254 | 0.239 | 0.225 | 0.224 | 0.24 | 0.142 | 0.268 | 0.22 | 0.263 | 0.237 | 0.209 | 0.246 | 0.197 | 0.248 | 0.198 | 7.314 | 0
| Well 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0
| Total | 0.242 | 0.253 | 0.243 | 0.239 | 0.235 | 0.239 | 0.285 | 0.26 | 0.242 | 0.249 | 0.245 | 0.241 | 0.217 | 0.24 | 0.251 | 0.233 | 0.254 | 0.239 | 0.225 | 0.224 | 0.24 | 0.142 | 0.268 | 0.22 | 0.263 | 0.237 | 0.209 | 0.246 | 0.197 | 0.248 | 0.198 | 7.324

## Monthly
System | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-17 | 2019-10-17 | 2019-11-17 | 2019-12-17
Cypress Lakes | 5633000 | 5732000 | 7211000 | 7326000 | 7746000 | 7602000 | 7501000 | 7680000 | 6575000 | 6510000 | 6817000 | 7324000