## WLU
2019 | Jan Used | Jan Loss | Feb Used | Feb Loss | March Used | March Loss | April Used | April Loss | May Used | May Loss | June Used | June Loss | July Used | July Loss | Aug Used | Aug Loss | Sept Used | Sept Loss | Oct Used | Oct Loss | Nov Used | Nov Loss | Dec Used | Dec Loss | YTD Total
Sanlando - Des Pinar | 0.0721 | 0.002831 | 0.03455 | 2.256 | 0.0309 | 0 | 0.0696 | 0.00932 | 0.0296 | 0.0704 | 0.0296 | 0.0072 | 0.031 | 0 | 0.02 | 0 | 0.0463 | 0 | 0 | 0 | 0.071325 | 0 | 0.02 | 0 | 2.8007
Sanlando - Knollwood | 0.0031 | 0 | 0.0033 | 0 | 0.00404 | 0 | 0.00604 | 0 | 0.00745 | 0 | 0.0086 | 0 | 0.00904 | 0 | 0.00922 | 0 | 0.00922 | 0 | 0.01191 | 0 | 0.01187 | 0 | 0.00923 | 0 | 0.09302
Sanlando - Wekiva | 0.010249 | 0.76258 | 0.01107 | 0.47282 | 0.24542 | 0.361 | 0.19506 | 0.24929 | 0.025339 | 0.02401 | 0.029012 | 0.16256 | 0.046248 | 0.74309 | 0.005845 | 0.72395 | 0.037019 | 2.119 | 0.012457 | 0.325 | 0.029522 | 1.0265 | 0.006155 | 0.2265 | 7.8497
Total | 0.85086 |  | 2.7777 |  | 0.64136 |  | 0.52931 |  | 0.1568 |  | 0.23697 |  | 0.82938 |  | 0.75901 |  | 2.2115 |  | 0.34937 |  | 1.1393 |  | 0.26188

## Monthly
System | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-17 | 2019-10-17 | 2019-11-17 | 2019-12-17
Sanlando-Des Pinar | 54533350 | 50424820 | 62911180 | 60404200 | 76239400 | 59846400 | 58964250 | 47423470 | 59057800 | 56442000 | 54832000 | 47084000
Sanlando-Knollwood | 371000 | 118100 | 1088700 | 1745600 | 2573300 | 1867200 | 1979500 | 1034700 | 2067700 | 1769100 | 852200 | 614000
Sanlando-Wekiva | 108299300 | 95926390 | 126291600 | 124760600 | 147421800 | 132215600 | 128570700 | 118439300 | 122689900 | 120453500 | 116135400 | 111718600
Sanlando- I/C (Purch) | 1000 | 83000 | 0 | 0 | 0 | 0 | 0 | 6000 | 0 | 0 | 0 | 2000

## Sanlando
255/368 - Sanlando - Wekiva, Des Pinar and Knollwood
PWS ID No. 3591121
CUP No. 160 |  | 10.098 mgd |  | Exp. Date: 08/07/22
FDEP Permitted Max Day Capacity of Plants:
| Des Pinar | 6.261 | mgd
| Knollwood | 0.576 | mgd
| Wekiva | 11.088 | mgd
Seminole County Acct: 52611-664784
Mirror Lake I/C
Hyper Links'!A1 | Des Pinar |  |  | Knollwood |  |  | Wekiva | [8 empty] | Total Water Used/Loss Des Pinar |  |  | Total Water Used/Loss Knollwood |  |  | Total Water Used/Loss Wekiva | [8 empty] | Source Meter Error Adj. | [10 empty] | Previous |  | Current
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Pumped | Pumped Daily Avg. | Pumped Daily Max. | Pumped | Pumped Daily Avg. | Pumped Daily Max. |  |  | Total Wekiva Pumped | Comb. Daily Max. | Total Pumped w/o Mirror Lk I/C | Total Pumped Inc. Mirror Lk I/C | Gallons Used | Gallons Loss | Total Used/ Loss | Gallons Used | Gallons Loss | Total Used/ Loss | Gallons Used | Gallons Loss | Total Used/ Loss | Total Gallons Loss/Used | Pumped, Less Gallons Loss/ Used | Billed Consumption (see Reuse Billing Tab) | AFW (%) Actual | Rainfall | Well Meter Pumped Reported to SJWMD | Wekiva (East & West Finish Flow Mtrs.) | Des Pinar (Red & Green Finish Flow Mtrs.) | Total Meter Adj. | Pumped, + Source Mtr Error, - Gallons Loss/ Used | Total AFW (Total Used/Loss + Billed) | AFW % plus source mtr. Error - HSPs** | Adjusted Well Totals (see well summary tab) + I/C Mirror Lake | Billed+ WLU = Total Accounted for. | Accounted for Water/Wells =% | Difference between HSP &Wells AFW. |  | Meter Read Date | Meter Read | Read Date | Read | Wtr Usage | UI Prior Read | UI Curr.Read | UI Flow
2019-01-01 | 56.071 | 1.8087 | 2.68 | 0.52368 | 0.016893 | 0.045632 | 124.53 | 4.0171 | 6.07 |  |  | 124.53 | 8.7956 | 181.1247 | 181.1257 | 0.0721 | 0.002831 | 0.074931 | 0.0031 | 0 | 0.0031 | 0.010249 | 0.76258 | 0.77283 | 0.85086 | 180.2748 | 140.0512 |  |  |  | 0 | 0 | 0 | 180.2748 | 140.9021 | 77.79% | 162.7661 | 140.9021 | 86.57% | -8.775% | 2019-01-01 | 2018-12-19 | 17007 | 2019-01-18 | 17007 | 0 | 0 | 0 | 0
February | 50.886 | 1.8174 | 3.304 | 0.4636 | 0.016557 | 0.033822 | 102.428 | 3.6581 | 6.479 |  |  | 102.428 | 9.8168 | 153.7776 | 153.8606 | 0.03455 | 2.256 | 2.2906 | 0.0033 | 0 | 0.0033 | 0.01107 | 0.47282 | 0.48389 | 2.7777 | 151.0829 | 117.7314 |  |  |  | 0 | 0 | 0 | 151.0829 | 120.5092 | 78.32% | 148.1229 | 120.5092 | 81.36% | -3.034% | Feb | 2019-01-18 | 17007 | 2019-02-19 | 17842 | 0.0835 |  |  | 0.084
March | 63.849 | 2.0596 | 3.414 | 1.696 | 0.05471 | 0.26851 | 147.967 | 4.7731 | 6.437 |  |  | 147.967 | 10.1195 | 213.512 | 213.512 | 0.0309 | 0 | 0.0309 | 0.00404 | 0 | 0.00404 | 0.24542 | 0.361 | 0.60642 | 0.64136 | 212.8707 | 145.6373 |  |  |  | 0 | 0 | 0 | 212.8707 | 146.2787 | 68.51% | 190.9957 | 146.2787 | 76.59% | -8.077% | March | 2019-02-19 | 17842 | 2019-03-20 | 17842 | 0 |  |  | 0
April | 61.123 | 2.0374 | 3.281 | 2.4032 | 0.080106 | 0.16631 | 141.626 | 4.5686 | 7.003 |  |  | 141.626 | 10.4503 | 205.1522 | 205.1522 | 0.0696 | 0.00932 | 0.07892 | 0.00604 | 0 | 0.00604 | 0.19506 | 0.24929 | 0.44435 | 0.52931 | 204.6229 | 176.9931 |  |  |  | 0 | 0 | 0 | 204.6229 | 177.5224 | 86.53% | 185.3354 | 177.5224 | 95.78% | -9.252% | April | 2019-03-20 | 17842 | 2019-04-19 | 17842 | 0 |  |  | 0
May | 75.967 | 2.4505 | 4.154 | 2.9652 | 0.095653 | 0.2328 | 184.202 | 5.942 | 8.094 |  |  | 184.202 | 12.4808 | 263.1342 | 263.1342 | 0.0296 | 0.0704 | 0.1 | 0.00745 | 0 | 0.00745 | 0.025339 | 0.02401 | 0.049349 | 0.1568 | 262.9774 | 223.0121 |  |  |  | 0 | 0 | 0 | 262.9774 | 223.1689 | 84.81% | 224.8766 | 223.1689 | 99.24% | -14.43% | May | 2019-04-19 | 17842 | 2019-05-21 | 17842 | 0 |  |  | 0
June | 59.253 | 1.9751 | 4.359 | 2.1899 | 0.072997 | 0.21795 | 159.863 | 5.1569 | 7.302 |  |  | 159.863 | 11.879 | 221.3059 | 221.3059 | 0.0296 | 0.0072 | 0.0368 | 0.0086 | 0 | 0.0086 | 0.029012 | 0.16256 | 0.19157 | 0.23697 | 221.0689 | 171.12 |  |  |  | 0 | 0 | 0 | 221.0689 | 171.357 | 77.43% | 194.9172 | 171.357 | 87.91% | -10.48% | June | 2019-05-21 | 17842 | 2019-06-20 | 17843 | 0.0001 |  |  | 0
July | 59.218 | 1.9103 | 2.874 | 2.1923 | 0.07072 | 0.23525 | 159.511 | 5.1455 | 6.962 |  |  | 159.511 | 10.0712 | 220.9213 | 220.9213 | 0.031 | 0 | 0.031 | 0.00904 | 0 | 0.00904 | 0.046248 | 0.74309 | 0.78934 | 0.82938 | 220.0919 | 160.5092 |  |  |  | 0 | 0 | 0 | 220.0919 | 161.3386 | 73.03% | 190.5291 | 161.3386 | 84.68% | -11.65% | July | 2019-06-20 | 17843 | 2019-07-19 | 17844 | 0.0001 |  |  | 0
August | 46.342 | 1.4949 | 2.003 | 1.1569 | 0.03732 | 0.070734 | 135.143 | 4.3595 | 6.933 |  |  | 135.143 | 9.0067 | 182.6419 | 182.6479 | 0.02 | 0 | 0.02 | 0.00922 | 0 | 0.00922 | 0.005845 | 0.72395 | 0.72979 | 0.75901 | 181.8889 | 144.0177 |  |  |  | 0 | 0 | 0 | 181.8889 | 144.7767 | 79.27% | 168.024 | 144.7767 | 86.16% | -6.899% | Aug | 2019-07-19 | 17844 | 2019-08-20 | 17853 | 0.0009 |  |  | 0.006
September | 59.582 | 1.9861 | 3.107 | 2.0798 | 0.069327 | 0.1922 | 145.317 | 4.8439 | 6.895 |  |  | 145.317 | 10.1942 | 206.9788 | 206.9788 | 0.0463 | 0 | 0.0463 | 0.00922 | 0 | 0.00922 | 0.037019 | 2.119 | 2.156 | 2.2115 | 204.7673 | 155.6757 |  |  |  | 0 | 0 | 0 | 204.7673 | 157.8872 | 76.28% | 184.6918 | 157.8872 | 85.49% | -9.205% | Sept | 2019-08-20 | 17853 | 2019-09-19 | 17853 | 0 |  |  | 0
October | 56.484 | 1.8221 | 3.025 | 1.805 | 0.058227 | 0.19025 | 133.112 | 4.2939 | 6.701 |  |  | 133.112 | 9.9163 | 191.401 | 191.401 | 0 | 0 | 0 | 0.01191 | 0 | 0.01191 | 0.012457 | 0.325 | 0.33746 | 0.34937 | 191.0517 | 159.9715 |  |  |  | 0 | 0 | 0 | 191.0517 | 160.3209 | 83.76% | 179.5665 | 160.3209 | 89.28% | -5.52% | Oct | 2019-09-19 | 17853 | 2019-10-21 | 17853 | 0 |  |  | 0
November | 55.407 | 1.8469 | 2.872 | 0.94293 | 0.031431 | 0.066704 | 147.97 | 4.9323 | 6.659 |  |  | 147.97 | 9.5977 | 204.3199 | 204.3199 | 0.071325 | 0 | 0.071325 | 0.01187 | 0 | 0.01187 | 0.029522 | 1.0265 | 1.0561 | 1.1393 | 203.1807 | 149.4283 |  |  |  | 0 | 0 | 0 | 203.1807 | 150.5676 | 73.69% | 172.8166 | 150.5676 | 87.13% | -13.43% | Nov | 2019-10-21 | 17853 | 2019-11-19 | 17866 | 0.0013 |  |  | 0
December | 46.49 | 1.4997 | 2.351 | 0.65254 | 0.02105 | 0.069262 | 118.854 | 3.834 | 6.476 |  |  | 118.854 | 8.8963 | 165.9965 | 165.9985 | 0.02 | 0 | 0.02 | 0.00923 | 0 | 0.00923 | 0.006155 | 0.2265 | 0.23266 | 0.26188 | 165.7367 | 140.6333 |  |  |  | 0 | 0 | 0 | 165.7367 | 140.8952 | 84.88% | 160.4828 | 140.8952 | 87.79% | -2.917% | Dec | 2019-11-19 | 17866 | 2019-12-19 | 17915 | 0.0049 |  |  | 0.002
YTD Total/Avg/Max | 690.672 | 1.8924 | 4.359 | 19.0712 | 0.052083 | 0.26851 | 1700.523 | 4.6271 | 8.094 |  |  | 1700.523 |  | 2410.2662 | 2410.3582 | 0.45498 | 2.3458 | 2.8007 | 0.09302 | 0 | 0.09302 | 0.6534 | 7.1963 | 7.8497 | 10.7435 | 2399.6147 | 1884.781 |  |  |  | 0 | 0 | 0 | 2399.6147 | 1895.5245
Total Proof to Daily Flow | 0 |  |  | 0 |  |  | 0 | [7 empty] | 181.1257 | [17 empty] | 0 |  | 140.9021 |  | YTD AFW% Jan - Dec |  | 87.63% | [6 empty] | 0.0908 |  |  | 0.092
[20 empty] | Des Pinar WLU Proof | 0 |  |  |  |  | Proof to Total Billed | 0
[20 empty] | Knollwood WLU Proof | 0
[20 empty] | Wekiva WLU Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
Water Loss-Use'!A1
Mirror Lake I/C
METER INFORMATION | SERIAL # | [5 empty] | Interconnect |  |  |  | Address |  | CC&B Acct# |  | CC&B Acct. Name |  |  | 2019-01-01 | 0.001 |  |  |  |  | 08/17/16 Knlwd Flow Meter Cal.
Des Pinar | [6 empty] | Meredith Manor I/C |  |  | Meredith Manor I/C | East Lake Brantley Dr. I/C |  | 5554789080 |  | Seminole County BBC |  |  | February | 0.083 |  |  |  |  | 0.00% Deviation
Plant Irrigation | 11824494 | [5 empty] | Wekiva Spring Lane I/C |  |  | Meredith Manor I/C | Wekiva Springs Lane I/C |  | 9152108311 |  | Seminole County BBC |  |  | March | 0 |  |  |  |  | Honeywell DR43000
Main Building/Shed | 97594024 | [5 empty] | Lake Brantley I/C |  |  | Lake Brantley I/C (Camellia & Azalea Dr.) | 2259 Camellia Dr. |  | 0806415065 |  | Seminole County BBC |  |  | April | 0 |  |  |  |  | SN: 16300006
I4 Irrigation Meter | 85706818 | [5 empty] | Mirror Lake I/C |  |  | Mirror Lake I/C (Wekiva to Sem. Cty.) | 3745 Retzer Dr. |  | 9834048777 |  | Seminole County BBC |  |  | May | 0
Main Gate Irrigation | 14619643 | [8 empty] | Bear Lake I/C | [7 empty] | June | 0 |  |  |  |  | Emailed JM/DH/FR & KS 03/27/19 about Jan. AFW
[18 empty] | July | 0
Knollwood | [17 empty] | August | 0.006
Plant Irrigation | 84542290 | [16 empty] | September | 0
Main Building | 14960090 | [16 empty] | October | 0
[18 empty] | November | 0
Wekiva | [17 empty] | December | 0.002
OP Build Hose Bibbs | 8222892
Hose Down WWTP | 86082007
Hose Down WWTP | 18476764
Shop Building | 91008934
Front Gate Irrigation | 91967327
Plant L/S | 8753257
OP Building | 32336395
Note on K15: Check the Wekiva daily read sheet attached to MOR for Emergency auto Interconnect usage.
Note on L15: Check the Wekiva daily read sheet attached to MOR for Emergency manual Interconnect usage.
Note on AB15: Peggy J. Hanks: Total does not include Reuse gallons.
Note on AF15: pjhanks: From Wekiva WTP 2016 Log
Note on AG15: pjhanks: From the Des Pinar 2016 WTP Log 02/04/16 mtr test/cal. 0% adj.
Note on AK15: Jacquee Chandler: HSP not used for Accounted for water but was used for MORs.
Note on AN15: Jacquee Chandler: Wells to be used for AFW & projections. Wells are NOT being used for the MORs, still using HSP for those.

## Daily Flow-368
255/368 Sanlando Utilities | [9 empty] | Hyper Links'!A1
Combined Daily Flow (Wekiva, Wekiva Interconnects, Des Pinar, Knollwood)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max
2019-01-01 | 5.9453 | 7.4686 | 7.181 | 6.7466 | 4.6604 | 6.3074 | 6.1467 | 4.9216 | 5.7452 | 7.126 | 4.407 | 6.6973 | 8.7779 | 7.0529 | 5.0561 | 6.4236 | 6.469 | 5.9859 | 6.5382 | 7.7639 | 4.9938 | 5.1744 | 6.0885 | 5.9337 | 4.1038 | 4.9231 | 5.5099 | 4.2856 | 3.3653 | 4.0987 | 5.2272 | 181.1247 | 5.8427 | 8.7779
February | 4.2252 | 4.7883 | 6.4038 | 5.721 | 3.6397 | 5.4541 | 5.9056 | 5.8071 | 5.7225 | 6.9126 | 4.461 | 3.43 | 4.2827 | 5.8408 | 4.3659 | 4.8821 | 6.8772 | 6.3184 | 5.5124 | 4.868 | 6.2854 | 5.3152 | 6.4815 | 9.058 | 7.0906 | 5.32 | 4.4521 | 4.3563 |  |  |  | 153.7776 | 5.4921 | 9.058
March | 4.6613 | 4.5823 | 9.2431 | 6.4072 | 4.5814 | 5.7208 | 6.0268 | 5.2 | 7.4879 | 9.1962 | 8.0517 | 6.5069 | 6.4825 | 7.703 | 6.4622 | 9.0132 | 9.5185 | 7.4098 | 4.9239 | 4.548 | 5.778 | 5.4534 | 6.6953 | 9.1465 | 7.8724 | 6.5915 | 7.0528 | 6.6693 | 6.3478 | 8.7876 | 9.3906 | 213.512 | 6.8875 | 9.5185
April | 8.664 | 4.7154 | 5.6862 | 7.1639 | 7.0279 | 4.5728 | 8.2968 | 6.6391 | 4.3374 | 4.9953 | 6.546 | 6.4702 | 7.1154 | 9.0156 | 6.4822 | 4.6663 | 7.4197 | 5.7518 | 7.3225 | 5.1219 | 6.7149 | 6.8305 | 6.2163 | 6.6959 | 8.3821 | 7.4028 | 7.1506 | 10.3873 | 9.0948 | 8.2666 |  | 205.1522 | 6.8384 | 10.3873
May | 8.7159 | 9.6555 | 6.7217 | 6.4015 | 10.761 | 5.7477 | 4.6864 | 7.6903 | 8.813 | 6.677 | 8.189 | 9.8281 | 6.5289 | 4.6797 | 5.5578 | 7.1988 | 6.5187 | 8.7594 | 9.7108 | 8.7938 | 8.212 | 9.7214 | 10.0624 | 9.7732 | 8.7706 | 10.9805 | 10.1234 | 10.9174 | 10.9914 | 11.8058 | 10.1415 | 263.1342 | 8.4882 | 11.8058
June | 10.4094 | 11.6817 | 10.1032 | 8.4726 | 9.918 | 9.9805 | 6.9417 | 7.2343 | 7.2317 | 5.6917 | 5.3642 | 5.2495 | 5.5788 | 4.2483 | 5.614 | 7.6463 | 5.2154 | 3.7911 | 4.7151 | 5.6743 | 4.3075 | 7.1937 | 9.0501 | 7.8456 | 8.4136 | 8.873 | 8.478 | 7.7772 | 8.641 | 9.9642 |  | 221.3059 | 7.3769 | 11.6817
July | 9.3333 | 8.2538 | 9.6672 | 9.9111 | 8.6497 | 7.1587 | 7.0921 | 6.2932 | 4.8336 | 6.6591 | 7.1915 | 6.1142 | 7.1986 | 8.4833 | 8.2094 | 6.8059 | 9.0887 | 6.5624 | 5.4814 | 6.7296 | 8.8879 | 6.625 | 6.3523 | 7.3484 | 6.2568 | 4.9486 | 4.907 | 7.7944 | 6.3837 | 4.9053 | 6.795 | 220.9213 | 7.1265 | 9.9111
August | 6.2206 | 4.2295 | 4.3267 | 5.8673 | 6.6939 | 5.7673 | 6.1411 | 6.1403 | 4.9349 | 6.2333 | 7.974 | 6.7306 | 3.7087 | 5.4602 | 5.0776 | 5.1233 | 4.4394 | 6.63 | 7.7477 | 5.2575 | 5.8952 | 7.2154 | 7.2368 | 6.9485 | 8.1827 | 8.7067 | 3.8671 | 5.6525 | 5.8443 | 4.7677 | 3.6209 | 182.6419 | 5.8917 | 8.7067
September | 5.5247 | 4.1511 | 3.8887 | 3.6963 | 4.3054 | 3.9016 | 5.8907 | 8.435 | 8.5961 | 7.2156 | 8.4901 | 8.2151 | 5.6553 | 5.7207 | 6.2901 | 5.6152 | 5.066 | 7.2881 | 7.389 | 7.657 | 4.7508 | 9.7646 | 7.6195 | 6.5888 | 8.8957 | 9.7909 | 8.8574 | 9.0862 | 9.8363 | 8.7967 |  | 206.9788 | 6.8993 | 9.8363
October | 7.2864 | 8.0737 | 8.6335 | 8.6205 | 9.1443 | 9.5123 | 6.9235 | 4.1028 | 4.8808 | 5.0267 | 4.4157 | 5.5334 | 7.8575 | 7.9016 | 6.2027 | 7.5089 | 7.1384 | 6.1242 | 4.9492 | 4.671 | 5.3707 | 3.9273 | 5.4127 | 6.1175 | 4.6314 | 4.463 | 4.758 | 5.2344 | 3.9666 | 6.3211 | 6.6912 | 191.401 | 6.1742 | 9.5123
November | 6.8884 | 5.5727 | 9.0687 | 7.9553 | 5.5468 | 5.9393 | 6.93 | 6.4093 | 5.8074 | 5.7488 | 7.055 | 5.6077 | 7.1288 | 7.0114 | 5.1947 | 6.7561 | 4.9797 | 7.2232 | 5.9485 | 7.3385 | 8.075 | 6.8106 | 7.5417 | 9.5905 | 6.9271 | 5.4334 | 7.5114 | 8.3692 | 6.2573 | 7.6932 |  | 204.3199 | 6.8107 | 9.5905
December | 8.1502 | 7.9541 | 5.1965 | 6.646 | 7.4399 | 6.0313 | 7.3204 | 8.5583 | 8.1922 | 5.7155 | 7.4956 | 7.2663 | 2.6647 | 4.3668 | 5.6161 | 5.3406 | 4.3276 | 4.267 | 4.5905 | 3.2162 | 5.0911 | 5.7062 | 3.2168 | 2.6069 | 5.2496 | 5.2535 | 3.6356 | 4.7433 | 4.5652 | 2.8876 | 2.6852 | 165.9965 | 5.3547 | 8.5583
Max. Day Combined | 10.4094 | 11.6817 | 10.1032 | 9.9111 | 10.761 | 9.9805 | 8.2968 | 8.5583 | 8.813 | 9.1962 | 8.4901 | 9.8281 | 8.7779 | 9.0156 | 8.2094 | 9.0132 | 9.5185 | 8.7594 | 9.7108 | 8.7938 | 8.8879 | 9.7646 | 10.0624 | 9.7732 | 8.8957 | 10.9805 | 10.1234 | 10.9174 | 10.9914 | 11.8058 | 10.1415 | 263.1342
Wekiva
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 4.791 | 5.308 | 4.995 | 5.367 | 2.687 | 4.335 | 4.79 | 3.602 | 3.831 | 5.195 | 2.7 | 4.411 | 6.07 | 5.324 | 3.703 | 4.242 | 4.54 | 4.135 | 4.452 | 5.445 | 3.742 | 3.642 | 4.164 | 4.055 | 2.606 | 2.734 | 3.565 | 2.69 | 1.977 | 2.661 | 2.771 | 124.53 | 4.0171 | 6.07 | 0
February | 3.56 | 2.747 | 4.068 | 4.362 | 2.313 | 3.688 | 4.055 | 3.698 | 3.582 | 4.737 | 2.968 | 2.127 | 2.87 | 2.503 | 3.021 | 2.903 | 4.438 | 4.938 | 3.68 | 3.469 | 4.218 | 3.654 | 4.005 | 6.479 | 5.306 | 3.573 | 2.9 | 2.566 |  |  |  | 102.428 | 3.6581 | 6.479 | 0
March | 2.936 | 2.79 | 6.415 | 5.117 | 3.211 | 3.575 | 4.136 | 3.871 | 4.968 | 6.135 | 5.943 | 4.504 | 4.01 | 5.468 | 4.813 | 6.436 | 6.038 | 5.592 | 3.467 | 2.721 | 3.77 | 3.702 | 4.574 | 6.24 | 6.437 | 4.616 | 4.762 | 4.363 | 4.923 | 6.359 | 6.075 | 147.967 | 4.7731 | 6.437 | 0
April | 7.003 | 2.987 | 3.534 | 4.86 | 5.196 | 2.681 | 5.764 | 5.263 | 2.633 | 3.035 | 4.213 | 4.794 | 4.828 | 6.307 | 5.325 | 3.021 | 4.599 | 3.354 | 5.889 | 2.961 | 4.153 | 5.135 | 4.619 | 3.999 | 5.929 | 5.467 | 4.588 | 6.94 | 6.743 | 5.806 | 0 | 141.626 | 4.5686 | 7.003 | 0
May | 6.142 | 6.698 | 4.955 | 4.665 | 6.512 | 4.444 | 3.147 | 5.329 | 6.077 | 4.982 | 6.075 | 6.703 | 5.125 | 3.355 | 3.531 | 5.065 | 5.003 | 6.293 | 6.415 | 6.715 | 6.134 | 6.589 | 7.016 | 7.06 | 5.824 | 6.621 | 8.094 | 7.273 | 7.326 | 7.674 | 7.36 | 184.202 | 5.942 | 8.094 | 0
June | 7.302 | 7.123 | 7.274 | 6.359 | 7.137 | 7.165 | 5.412 | 5.385 | 5.065 | 4.405 | 4.115 | 3.871 | 3.99 | 3.266 | 4.047 | 5.581 | 4.044 | 2.929 | 3.251 | 4.134 | 3.196 | 5.144 | 6.406 | 6.264 | 6.317 | 6.521 | 5.71 | 5.614 | 6.116 | 6.72 | 0 | 159.863 | 5.1569 | 7.302 | 0
July | 6.962 | 5.801 | 6.592 | 6.933 | 6.545 | 4.583 | 4.94 | 4.888 | 3.411 | 4.665 | 5.259 | 4.721 | 5.336 | 6.078 | 6.264 | 5.108 | 6.286 | 5.175 | 3.584 | 4.976 | 5.869 | 5.181 | 4.782 | 5.214 | 4.436 | 3.68 | 3.366 | 5.464 | 5.295 | 3.478 | 4.639 | 159.511 | 5.1455 | 6.962 | 0
August | 4.563 | 3.251 | 2.904 | 3.943 | 5.246 | 4.344 | 4.543 | 4.255 | 3.722 | 4.517 | 6.229 | 4.984 | 2.808 | 3.981 | 3.587 | 3.902 | 2.883 | 5.223 | 5.692 | 3.933 | 4.233 | 5.584 | 5.663 | 5.362 | 6.131 | 6.933 | 2.553 | 3.926 | 4.294 | 3.57 | 2.384 | 135.143 | 4.3595 | 6.933 | 0
September | 3.859 | 3.149 | 2.556 | 2.409 | 2.854 | 2.772 | 4.294 | 6.187 | 6.349 | 5.18 | 5.872 | 5.593 | 4.238 | 3.777 | 4.187 | 4.091 | 3.574 | 4.806 | 5.213 | 5.849 | 2.768 | 6.895 | 5.398 | 4.899 | 6.183 | 6.526 | 6.264 | 6.403 | 6.838 | 6.334 |  | 145.317 | 4.8439 | 6.895 | 0
October | 5.533 | 5.526 | 5.864 | 6.216 | 6.701 | 6.336 | 5.404 | 2.832 | 3.176 | 3.438 | 2.954 | 3.767 | 5.272 | 6.076 | 4.484 | 5.187 | 5.004 | 4.561 | 3.245 | 3.081 | 3.86 | 2.503 | 3.673 | 4.198 | 3.192 | 2.868 | 2.918 | 3.786 | 2.727 | 4.136 | 4.594 | 133.112 | 4.2939 | 6.701 | 0
November | 5.092 | 3.506 | 6.566 | 5.779 | 4.135 | 3.954 | 4.851 | 4.638 | 4.137 | 3.834 | 5.383 | 4.307 | 5.165 | 4.75 | 4.015 | 4.974 | 2.955 | 5.852 | 4.387 | 5.244 | 5.916 | 4.977 | 5.608 | 6.659 | 5.377 | 3.96 | 5.452 | 6.493 | 4.216 | 5.788 |  | 147.97 | 4.9323 | 6.659 | 0
December | 5.752 | 6.227 | 3.799 | 4.618 | 5.397 | 4.488 | 5.3 | 6.476 | 5.828 | 4.277 | 5.345 | 5.376 | 1.721 | 2.844 | 3.996 | 3.869 | 3.133 | 3.048 | 3.049 | 2.196 | 3.357 | 3.827 | 2.312 | 1.865 | 3.886 | 3.85 | 2.639 | 3.369 | 3.218 | 1.967 | 1.825 | 118.854 | 3.834 | 6.476 | 0
[32 empty] | 1700.523 | Grand Total
Des Pinar
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 1.149 | 2.127 | 2.171 | 1.371 | 1.953 | 1.952 | 1.349 | 1.312 | 1.882 | 1.916 | 1.697 | 2.257 | 2.68 | 1.72 | 1.344 | 2.136 | 1.901 | 1.842 | 2.062 | 2.307 | 1.246 | 1.526 | 1.891 | 1.864 | 1.492 | 2.161 | 1.92 | 1.588 | 1.38 | 1.432 | 2.443 | 56.071 | 1.8087 | 2.68 | 0
February | 0.659 | 2.019 | 2.31 | 1.351 | 1.318 | 1.749 | 1.836 | 2.096 | 2.114 | 2.162 | 1.483 | 1.291 | 1.407 | 3.304 | 1.331 | 1.959 | 2.416 | 1.371 | 1.815 | 1.389 | 2.045 | 1.648 | 2.461 | 2.56 | 1.767 | 1.733 | 1.534 | 1.758 |  |  |  | 50.886 | 1.8174 | 3.304 | 0
March | 1.71 | 1.758 | 2.808 | 1.27 | 1.353 | 2.119 | 1.859 | 1.312 | 2.483 | 3.024 | 2.087 | 1.98 | 2.444 | 2.2 | 1.627 | 2.556 | 3.414 | 1.792 | 1.436 | 1.785 | 1.965 | 1.728 | 2.052 | 2.638 | 1.292 | 1.885 | 2.196 | 2.217 | 1.388 | 2.292 | 3.179 | 63.849 | 2.0596 | 3.414 | 0
April | 1.571 | 1.697 | 2.132 | 2.22 | 1.749 | 1.816 | 2.448 | 1.334 | 1.647 | 1.899 | 2.247 | 1.636 | 2.173 | 2.565 | 1.118 | 1.565 | 2.692 | 2.312 | 1.383 | 2.119 | 2.48 | 1.655 | 1.54 | 2.565 | 2.342 | 1.847 | 2.48 | 3.281 | 2.255 | 2.355 |  | 61.123 | 2.0374 | 3.281 | 0
May | 2.427 | 2.801 | 1.702 | 1.654 | 4.139 | 1.258 | 1.495 | 2.191 | 2.624 | 1.66 | 2.026 | 3.032 | 1.38 | 1.298 | 1.924 | 2.054 | 1.464 | 2.375 | 3.169 | 2.023 | 2.03 | 3.003 | 2.938 | 2.687 | 2.781 | 4.154 | 2.006 | 3.578 | 3.464 | 3.899 | 2.731 | 75.967 | 2.4505 | 4.154 | 0
June | 2.943 | 4.359 | 2.734 | 2.035 | 2.563 | 2.674 | 1.502 | 1.775 | 2.121 | 1.26 | 1.22 | 1.358 | 1.573 | 0.955 | 1.529 | 2.009 | 1.15 | 0.845 | 1.449 | 1.511 | 1.082 | 1.963 | 2.532 | 1.535 | 2.049 | 2.262 | 2.652 | 2.122 | 2.421 | 3.07 |  | 59.253 | 1.9751 | 4.359 | 0
July | 2.26 | 2.408 | 2.84 | 2.763 | 2.07 | 2.484 | 2.087 | 1.384 | 1.394 | 1.913 | 1.875 | 1.357 | 1.811 | 2.322 | 1.895 | 1.673 | 2.596 | 1.341 | 1.87 | 1.667 | 2.874 | 1.429 | 1.555 | 2.055 | 1.776 | 1.241 | 1.498 | 2.263 | 1.06 | 1.385 | 2.072 | 59.218 | 1.9103 | 2.874 | 0
August | 1.645 | 0.958 | 1.413 | 1.899 | 1.438 | 1.385 | 1.547 | 1.846 | 1.176 | 1.673 | 1.678 | 1.713 | 0.843 | 1.466 | 1.477 | 1.192 | 1.509 | 1.375 | 2.003 | 1.297 | 1.612 | 1.565 | 1.509 | 1.561 | 1.989 | 1.703 | 1.304 | 1.665 | 1.529 | 1.156 | 1.216 | 46.342 | 1.4949 | 2.003 | 0
September | 1.653 | 0.997 | 1.321 | 1.277 | 1.428 | 1.094 | 1.542 | 2.171 | 2.17 | 2.002 | 2.475 | 2.499 | 1.401 | 1.881 | 2.058 | 1.513 | 1.465 | 2.349 | 2.096 | 1.769 | 1.902 | 2.716 | 2.182 | 1.644 | 2.535 | 3.107 | 2.557 | 2.491 | 2.849 | 2.438 |  | 59.582 | 1.9861 | 3.107 | 0
October | 1.729 | 2.387 | 2.591 | 2.363 | 2.253 | 3.025 | 1.477 | 1.254 | 1.666 | 1.576 | 1.427 | 1.701 | 2.503 | 1.78 | 1.695 | 2.211 | 2.058 | 1.532 | 1.663 | 1.57 | 1.507 | 1.406 | 1.657 | 1.86 | 1.415 | 1.566 | 1.811 | 1.423 | 1.216 | 2.119 | 2.043 | 56.484 | 1.8221 | 3.025 | 0
November | 1.791 | 2 | 2.443 | 2.168 | 1.405 | 1.924 | 2.015 | 1.766 | 1.646 | 1.884 | 1.665 | 1.294 | 1.905 | 2.222 | 1.173 | 1.747 | 1.978 | 1.365 | 1.549 | 2.054 | 2.12 | 1.823 | 1.883 | 2.872 | 1.541 | 1.462 | 2 | 1.834 | 2.034 | 1.844 |  | 55.407 | 1.8469 | 2.872 | 0
December | 2.345 | 1.712 | 1.375 | 1.979 | 1.983 | 1.534 | 1.954 | 2.013 | 2.351 | 1.431 | 2.082 | 1.854 | 0.937 | 1.491 | 1.597 | 1.464 | 1.192 | 1.208 | 1.524 | 1.019 | 1.703 | 1.859 | 0.904 | 0.741 | 1.359 | 1.4 | 0.995 | 1.367 | 1.341 | 0.918 | 0.858 | 46.49 | 1.4997 | 2.351 | 0
[32 empty] | 690.672 | Grand Total
Knollwood
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.005334 | 0.033564 | 0.015042 | 0.008633 | 0.020409 | 0.020408 | 0.00773 | 0.007593 | 0.032177 | 0.014957 | 0.010041 | 0.029293 | 0.027914 | 0.008901 | 0.00908 | 0.045632 | 0.028022 | 0.00893 | 0.024183 | 0.011867 | 0.005795 | 0.006431 | 0.033523 | 0.014741 | 0.005811 | 0.028121 | 0.024864 | 0.007578 | 0.008251 | 0.00569 | 0.013167 | 0.52368 | 0.016893 | 0.045632 | 0
February | 0.006221 | 0.022329 | 0.025773 | 0.008048 | 0.008666 | 0.017064 | 0.014565 | 0.013068 | 0.026534 | 0.013565 | 0.009978 | 0.011971 | 0.005725 | 0.033822 | 0.013911 | 0.020094 | 0.023207 | 0.009418 | 0.017396 | 0.009998 | 0.022443 | 0.013248 | 0.015484 | 0.019042 | 0.017621 | 0.013952 | 0.018142 | 0.03232 |  |  |  | 0.4636 | 0.016557 | 0.033822 | 0
March | 0.015293 | 0.034254 | 0.020092 | 0.020201 | 0.017434 | 0.026817 | 0.03181 | 0.017022 | 0.036933 | 0.037203 | 0.021715 | 0.022859 | 0.028459 | 0.035006 | 0.022172 | 0.021229 | 0.06652 | 0.025783 | 0.020949 | 0.041995 | 0.043033 | 0.023412 | 0.069316 | 0.26851 | 0.14339 | 0.090541 | 0.094806 | 0.089284 | 0.036762 | 0.13661 | 0.13661 | 1.696 | 0.05471 | 0.26851 | 0
April | 0.089977 | 0.031416 | 0.020186 | 0.083908 | 0.082949 | 0.075796 | 0.084752 | 0.042066 | 0.057408 | 0.061284 | 0.085984 | 0.040238 | 0.11439 | 0.14358 | 0.039188 | 0.080271 | 0.12875 | 0.085828 | 0.050509 | 0.041939 | 0.081939 | 0.040523 | 0.057305 | 0.13185 | 0.11109 | 0.088785 | 0.0826 | 0.16631 | 0.096794 | 0.10558 |  | 2.4032 | 0.080106 | 0.16631 | 0
May | 0.1469 | 0.15652 | 0.064687 | 0.0825 | 0.11005 | 0.045701 | 0.044407 | 0.17027 | 0.11195 | 0.03498 | 0.087981 | 0.093128 | 0.023853 | 0.026691 | 0.10276 | 0.079808 | 0.051666 | 0.091368 | 0.12676 | 0.055768 | 0.047961 | 0.12942 | 0.10836 | 0.026185 | 0.16557 | 0.20554 | 0.023357 | 0.066441 | 0.20137 | 0.2328 | 0.050503 | 2.9652 | 0.095653 | 0.2328 | 0
June | 0.16442 | 0.19967 | 0.095248 | 0.078565 | 0.21795 | 0.14155 | 0.027746 | 0.074344 | 0.045749 | 0.026738 | 0.029177 | 0.020539 | 0.015762 | 0.027259 | 0.038023 | 0.056313 | 0.021413 | 0.017139 | 0.015072 | 0.029335 | 0.029461 | 0.086735 | 0.1121 | 0.046628 | 0.047618 | 0.089996 | 0.116 | 0.041201 | 0.10395 | 0.17421 |  | 2.1899 | 0.072997 | 0.21795 | 0
July | 0.11133 | 0.044849 | 0.23525 | 0.21508 | 0.034665 | 0.091666 | 0.065078 | 0.021155 | 0.028619 | 0.081109 | 0.057475 | 0.036174 | 0.051578 | 0.083294 | 0.050375 | 0.024859 | 0.20674 | 0.046402 | 0.027411 | 0.086606 | 0.14494 | 0.015023 | 0.015301 | 0.079434 | 0.044845 | 0.02756 | 0.043019 | 0.067443 | 0.028736 | 0.042338 | 0.083965 | 2.1923 | 0.07072 | 0.23525 | 0
August | 0.012603 | 0.020478 | 0.009679 | 0.025297 | 0.009944 | 0.038311 | 0.051083 | 0.039262 | 0.036941 | 0.043304 | 0.066989 | 0.033633 | 0.05769 | 0.013211 | 0.013637 | 0.029274 | 0.047357 | 0.031995 | 0.05275 | 0.027534 | 0.050216 | 0.066437 | 0.064775 | 0.025506 | 0.062705 | 0.070734 | 0.010098 | 0.061544 | 0.021281 | 0.041701 | 0.020936 | 1.1569 | 0.03732 | 0.070734 | 0
September | 0.01266 | 0.00512 | 0.011675 | 0.010261 | 0.023406 | 0.035557 | 0.054679 | 0.077004 | 0.077083 | 0.03361 | 0.14312 | 0.12313 | 0.016319 | 0.062718 | 0.045103 | 0.011174 | 0.027044 | 0.13311 | 0.080024 | 0.038966 | 0.080781 | 0.15363 | 0.039511 | 0.045842 | 0.17774 | 0.15786 | 0.036439 | 0.1922 | 0.14934 | 0.024707 |  | 2.0798 | 0.069327 | 0.1922 | 0
October | 0.024397 | 0.16068 | 0.17853 | 0.041546 | 0.19025 | 0.15133 | 0.042489 | 0.016845 | 0.038786 | 0.012656 | 0.034666 | 0.065351 | 0.082534 | 0.045606 | 0.023732 | 0.11087 | 0.076434 | 0.031181 | 0.041161 | 0.02002 | 0.0037 | 0.018281 | 0.082691 | 0.059491 | 0.024393 | 0.029033 | 0.029033 | 0.025402 | 0.023566 | 0.066121 | 0.054245 | 1.805 | 0.058227 | 0.19025 | 0
November | 0.005418 | 0.066704 | 0.059673 | 0.008335 | 0.006821 | 0.061336 | 0.064047 | 0.00533 | 0.02436 | 0.030786 | 0.007041 | 0.006707 | 0.058845 | 0.039449 | 0.006654 | 0.035103 | 0.046736 | 0.006235 | 0.012505 | 0.040469 | 0.039007 | 0.010596 | 0.050659 | 0.059534 | 0.009126 | 0.011426 | 0.059387 | 0.042158 | 0.007299 | 0.061184 |  | 0.94293 | 0.031431 | 0.066704 | 0
December | 0.053231 | 0.0151 | 0.022502 | 0.048966 | 0.059909 | 0.009316 | 0.066415 | 0.069262 | 0.013171 | 0.007513 | 0.068566 | 0.036298 | 0.006661 | 0.031816 | 0.023075 | 0.007597 | 0.002573 | 0.010953 | 0.017533 | 0.001174 | 0.031129 | 0.020203 | 0.000784 | 0.000851 | 0.004621 | 0.003455 | 0.001592 | 0.007266 | 0.006194 | 0.002621 | 0.002193 | 0.65254 | 0.02105 | 0.069262 | 0
[32 empty] | 19.0712 | Grand Total
Mirror Lake InterConnect
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 3.2258e-05 | 0.001
February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0.083 | 0.0029643 | 0.083
March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.00019355 | 0.006
September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 6.4516e-05 | 0.002
[32 empty] | 0.092 | Grand Total

## Sanlando Well Summary
255/368 (680) - Sanlando Utilities - Wells Only
Hyper Links'!A1 | Des Pinar |  |  |  |  | Knollwood |  |  |  |  | Wekiva
| Total Pumped | Source Mtr. Error Adj. | Adj. Total Pumped (Pumped + Mtr Error) | Pumped Daily Avg. | Pumped Daily Max. | Total Pumped | Source Mtr. Error Adj. | Adj. Total Pumped (Pumped + Mtr Error) | Pumped Daily Avg. | Pumped Daily Max. | Total Pumped | Source Mtr. Error Adj. | Adj. Total Pumped (Pumped + Mtr Error) | Pumped Daily Avg. | Pumped Daily Max. | Sem. Cty Mirror Lk. To Wekiva | Orange Cty I/C to Wekiva | Total Wekiva Pumped (Inc. I/C) | Comb. Daily Max. | Total Pumped | AFW (%) Actual | Rainfall | Well Meter Pumped Reported to SJWMD | Adj. Well Flows | Adjusted Well Totals | Billed+ WLU
2019-01-01 | 54.5333 | 0.84274 | 55.3761 | 1.7591 | 2.797 | 0.371 | 0.0004368 | 0.37144 | 0.011968 | 0.0838 | 108.2993 | -0.40463 | 107.8947 | 3.4935 | 4.1507 | 0.001 | 0 | 107.8957 | 7.0315 | 163.2037 |  |  |  | 0.43854 | 162.7661 | 140.9021 | 163203650
February | 50.4248 | 0.3594 | 50.7842 | 1.8009 | 3.346 | 0.1181 | 0.1181 | 0.2362 | 0.0042179 | 0.0331 | 95.9264 | -2.0481 | 93.8783 | 3.4259 | 4.2237 | 0.083 | 0 | 96.0094 | 7.6029 | 146.4693 |  |  |  | -1.5706 | 148.1229 | 120.5092 | 146469310
March | 62.9112 | 1.3952 | 64.3064 | 2.0294 | 3.603 | 1.0887 | 0.00022601 | 1.0889 | 0.035119 | 0.2856 | 126.2916 | -2.0996 | 124.192 | 4.0739 | 5.351 | 0 | 0 | 126.2916 | 9.2396 | 190.2915 |  |  |  | -0.70423 | 190.9957 | 146.2787 | 190291480
April | 60.4042 | 1.361 | 61.7652 | 2.0135 | 3.532 | 1.7456 | 0.0046159 | 1.7502 | 0.058187 | 0.1966 | 124.7606 | 0.20942 | 124.97 | 4.1587 | 5.8314 | 0 | 0 | 124.7606 | 9.56 | 186.9104 |  |  |  | 1.575 | 185.3354 | 177.5224 | 186910400
May | 76.2394 | 1.6797 | 77.9191 | 2.4593 | 4.703 | 2.5733 | 0.020202 | 2.5935 | 0.08301 | 0.3487 | 147.4218 | -0.34201 | 147.0798 | 4.7555 | 6.5969 | 0 | 0 | 147.4218 | 11.6486 | 226.2345 |  |  |  | 1.3579 | 224.8766 | 223.1689 | 226234500
June | 59.8464 | 1.2378 | 61.0842 | 1.9949 | 3.906 | 1.8672 | 0.014072 | 1.8813 | 0.06224 | 0 | 132.2156 | -2.2399 | 129.9757 | 0 | 0 | 0 | 0 | 132.2156 | 3.906 | 193.9292 |  |  |  | -0.98804 | 194.9172 | 171.357 | 193929200
July | 58.9642 | 1.2171 | 60.1814 | 1.9021 | 3.366 | 1.9795 | 0.015395 | 1.9949 | 0.063855 | 0.22 | 128.5707 | -2.2471 | 126.3236 | 4.1474 | 7.523 | 0 | 0 | 128.5707 | 11.109 | 189.5145 |  |  |  | -1.0146 | 190.5291 | 161.3386 | 189514450
August | 47.4235 | 1.0123 | 48.4357 | 1.5298 | 2.132 | 1.0347 | 0.0047068 | 1.0394 | 0.033377 | 0 | 118.4393 | -2.1374 | 116.3019 | 3.8206 | 5.4064 | 0.006 | 0 | 118.4453 | 7.5384 | 166.8975 |  |  |  | -1.1205 | 168.024 | 144.7767 | 166897470
September | 59.0578 | 1.2032 | 60.261 | 1.9686 | 3.175 | 2.0677 | 0.017218 | 2.0849 | 0.068923 | 0.3001 | 122.6899 | -2.0968 | 120.5931 | 4.0897 | 5.5943 | 0 | 0 | 122.6899 | 9.0694 | 183.8154 |  |  |  | -0.8764 | 184.6918 | 157.8872 | 183815400
October | 56.442 | 1.1518 | 57.5938 | 1.8207 | 4.135 | 1.7691 | 0.015317 | 1.7844 | 0.057068 | 0.3764 | 120.4535 | -2.069 | 118.3845 | 3.8856 | 5.8965 | 0 | 0 | 120.4535 | 10.4079 | 178.6646 |  |  |  | -0.90193 | 179.5665 | 160.3209 | 178664600
November | 54.832 | 1.1082 | 55.9402 | 1.8277 | 2.989 | 0.8522 | 0.0037796 | 0.85598 | 0.028407 | 0.0917 | 116.1354 | -2.109 | 114.0264 | 3.8712 | 4.631 | 0 | 0 | 116.1354 | 7.7117 | 171.8196 |  |  |  | -0.99698 | 172.8166 | 150.5676 | 171819600
December | 47.084 | 0.93246 | 48.0165 | 1.5188 | 2.761 | 0.614 | 0.0041647 | 0.61816 | 1.5188 | 2.761 | 111.7186 | -2.0008 | 109.7178 | 3.6038 | 6.441 | 0.002 | 0 | 111.7206 | 11.963 | 159.4166 |  |  |  | -1.0642 | 160.4828 | 140.8952 | 159416600
YTD Total/Avg/Max | 688.1629 | 13.5008 | 701.6637 | 1.8854 | 4.703 | 16.0811 | 0.21823 | 16.2993 | 0.16877 | 2.761 | 1452.9227 | -19.5851 | 1433.3376 | 3.6105 | 7.523 | 0.092 | 0 | 1452.6101 | 14.987 | 2157.1667 |  |  |  | -5.866 | 310.889 | 261.4112
Seminole County Emergency I/C Meters
[11 empty] | From Seminole to Sanlando: |  |  | SN 08689879
[11 empty] | From Sanlando to Seminole: |  |  | SN 08689880
Note on Q9: Check the Wekiva daily read sheet attached to MOR for Emergency auto Interconnect usage.
Note on R9: Check the Wekiva daily read sheet attached to MOR for Emergency manual Interconnect usage.

## Sanlando Wells
255/368 Sanlando Well Totals | [8 empty] | Hyper Links'!A1
| Des Pinar | [5 empty] | Source Meter Error Adj. - Des Pinar | [9 empty] | Source Meter Error Adj. - Des Pinar
| Well 1 | Well 1A | Well 2 | Well 2A | Total Wells | Des Pinar Proof | Well 1 Meter Adj. % 04/17/18 +0.50% 02/21/19 -1.01% | Well 1 Pumped Meter Error | Well 1A Meter Adj. % 04/17/18 +0.62% 02/21/19 0.66% | Well1A Pumped Meter Adj. | Well 2 Meter Adj. % 04/17/2019 +1.01% 02/21/19 1.60% | Well 2 Pumped Meter Adj. | Well 2A Meter Adj. % 04/17/18 -0.15%02/21/19 1.72% | Well 2A Pumped Meter Adj. | Total Adj. |  | Well 1 Meter Adj. % (05/12/17 -1.01%) 04/17/18 +0.50% | Well 1 Pumped Meter Error | Well 1A Meter Adj. % (05/12/17 -0.62%) 04/17/18 +0.62% | Well1A Pumped Meter Adj. | Well 2 Meter Adj. % (05/12/17 -0.06%) 04/17/2019 +1.01% | Well 2 Pumped Meter Adj. | Well 2A Meter Adj. % (05/12/17 +0.66%) 04/17/18 -0.15% | Well 2A Pumped Meter Adj. | Total Adj.
2019-01-01 | 0.00235 | 46.943 | 6.994 | 0.594 | 54.5333 | 0 | 0.5% | 1.175e-05 | 0.62% | 0.29105 | 1.01% | 0.55079 | 0.15% | 0.000891 | 0.84274 |  | -1.01% | -2.02e-06 | -0.62% | -0.15355 | -0.06% | -0.0016938 | 0.66% | 0.0119 | -0.14335 | 04/01-04/16
February | 0.00282 | 42.349 | 6.885 | 1.188 | 50.4248 | 0 |  | 0.00282 |  | 0.26696 |  | 0.080772 |  | 0.008847 | 0.3594 |  | 0.5% | 0 | 0.62% | 0.14917 | 1.01% | 0.045985 | -0.15% | -0.0036 | 0.19155 | 04/17-04/30
March | 0.00018 | 50.054 | 9.471 | 3.386 | 62.9112 | 0 | -1.01% | -1.818e-06 | 0.66% | 0.33036 | 1.6% | 1.0066 | 1.72% | 0.058239 | 1.3952 |  |  | -2.02e-06 |  | -0.0043834 |  | 0.044291 |  | 0.0082998 | 0.048206 | 1.3128
April | 0.0002 | 48.825 | 7.376 | 4.203 | 60.4042 | 0 | -1.01% | -2.02e-06 | 0.66% | 0.32225 | 1.6% | 0.96647 | 1.72% | 0.072292 | 1.361
May | 0.0004 | 49.885 | 18.758 | 7.596 | 76.2394 | 0 | -1.01% | -4.04e-06 | 0.66% | 0.32924 | 1.6% | 1.2198 | 1.72% | 0.13065 | 1.6797 |  | Source Meter Error Adj. - Des Pinar
June | 0.0004 | 30.918 | 24.5 | 4.428 | 59.8464 | 0 | -1.01% | -4.04e-06 | 0.66% | 0.20406 | 1.6% | 0.95754 | 1.72% | 0.076162 | 1.2378 |  | Well 1 Meter Adj. % 04/17/18 +0.50% 02/21/19 -1.01% | Well 1 Pumped Meter Error | Well 1A Meter Adj. % 04/17/18 +0.62% 02/21/19 0.66% | Well1A Pumped Meter Adj. | Well 2 Meter Adj. % 04/17/2019 +1.01% 02/21/19 1.60% | Well 2 Pumped Meter Adj. | Well 2A Meter Adj. % 04/17/18 -0.15%02/21/19 1.72% | Well 2A Pumped Meter Adj. | Total Adj.
July | 0.00025 | 29.533 | 24.852 | 4.579 | 58.9642 | 0 | -1.01% | -2.525e-06 | 0.66% | 0.19492 | 1.6% | 0.94343 | 1.72% | 0.078759 | 1.2171 |  | 0.5% | 0.00282 | 0.62% | 0.19444 | 1.01% | 0.050308 | 0.15% | 0.001107 | 0.24868
August | 0.00047 | 17.48 | 21.913 | 8.03 | 47.4235 | 0 | -1.01% | -4.747e-06 | 0.66% | 0.11537 | 1.6% | 0.75878 | 1.72% | 0.13812 | 1.0123 |  | -1.01% | 0 | 0.66% | 0.072514 | 1.6% | 0.030464 | 1.72% | 0.00774 | 0.11072
September | 0.0018 | 31.532 | 24.608 | 2.916 | 59.0578 | 0 | -1.01% | -1.818e-05 | 0.66% | 0.20811 | 1.6% | 0.94492 | 1.72% | 0.050155 | 1.2032 |  |  | 0.00282 |  | 0.26696 |  | 0.080772 |  | 0.008847 | 0.3594
October | 0.003 | 28.197 | 24.6 | 3.642 | 56.442 | 0 | -1.01% | -3.03e-05 | 0.66% | 0.1861 | 1.6% | 0.90307 | 1.72% | 0.062642 | 1.1518
November | 0.002 | 23.892 | 26.679 | 4.259 | 54.832 | 0 | -1.01% | -2.02e-05 | 0.66% | 0.15769 | 1.6% | 0.87731 | 1.72% | 0.073255 | 1.1082
December | 0.002 | 20.189 | 24.225 | 2.668 | 47.084 | 0 | -1.01% | -2.02e-05 | 0.66% | 0.13325 | 1.6% | 0.75334 | 1.72% | 0.04589 | 0.93246
| Knollwood |  |  |  | Source Meter Adj. - Knollwood | [5 empty] | Source Meter Adj. - Knollwood 04/17/18
| Well 3 | Well 4 | Total Wells | Knollwood Proof | Well 3 Meter Adj. % 04/17/18 +0.74% 02/21/19 -1.27% | Well 3 Pumped Meter Adj. | Well 4 Meter Adj. % 04/17/18 -0.45% 02/21/19 1.48% | Well 4 Pumped Meter Adj. | Total Adj. |  | Well 3 Meter Adj. % (05/12/17 +0.99%) 04/17/18 +0.74% | Well 3 Pumped Meter Adj. | Well 4 Meter Adj. % (05/12/17 +1.82%) 04/17/18 -0.45% | Well 4 Pumped Meter Adj. | Total Adj.
2019-01-01 | 0.177 | 0.194 | 0.371 | 0 | 0.74% | 0.0013098 | -0.45% | -0.000873 | 0.0004368 |  | 0.99% | 0.4136 | 1.82% | 0.0069706 | 0.42057 | 04/01-04/16
February | 0.0421 | 0.076 | 0.1181 | 0 | .74% & -1.27% | 0.0421 | -0.45% & 1.48% | 0.076 | 0.1181 |  | 0.74% | 0.358 | -0.45% | -0.0026595 | 0.35534 | 04/17-04/30
March | 0.5777 | 0.511 | 1.0887 | 0 | -1.27% | -0.0073368 | 1.48% | 0.0075628 | 0.00022601 |  |  | 0.7716 |  | 0.0043111 | 0.7713
April | 0.7716 | 0.974 | 1.7456 | 0 | -1.27% | -0.0097993 | 1.48% | 0.014415 | 0.0046159
May | 0.6503 | 1.923 | 2.5733 | 0 | -1.27% | -0.0082588 | 1.48% | 0.02846 | 0.020202 |  | Source Meter Adj. - Knollwood
June | 0.4932 | 1.374 | 1.8672 | 0 | -1.27% | -0.0062636 | 1.48% | 0.020335 | 0.014072 |  | Well 3 Meter Adj. % 04/17/18 +0.74% 02/21/19 -1.27% | Well 3 Pumped Meter Adj. | Well 4 Meter Adj. % 04/17/18 -0.45% 02/21/19 1.48% | Well 4 Pumped Meter Adj. | Total Adj.
July | 0.5055 | 1.474 | 1.9795 | 0 | -1.27% | -0.0064199 | 1.48% | 0.021815 | 0.015395 |  | 0.74% | 0.0421 | -0.45% | 0.076 | 0.1181
August | 0.3857 | 0.649 | 1.0347 | 0 | -1.27% | -0.0048984 | 1.48% | 0.0096052 | 0.0047068 |  | -1.27% | 0 | 1.48% | 0 | 0
September | 0.4867 | 1.581 | 2.0677 | 0 | -1.27% | -0.0061811 | 1.48% | 0.023399 | 0.017218 |  |  | 0.0421 |  | 0.076 | 0.10278
October | 0.3951 | 1.374 | 1.7691 | 0 | -1.27% | -0.0050178 | 1.48% | 0.020335 | 0.015317
November | 0.3212 | 0.531 | 0.8522 | 0 | -1.27% | -0.0040792 | 1.48% | 0.0078588 | 0.0037796
December | 0.179 | 0.435 | 0.614 | 0 | -1.27% | -0.0022733 | 1.48% | 0.006438 | 0.0041647
| Wekiva | [6 empty] | Source Meter Error Adj. - Wekiva | [11 empty] | Source Meter Error Adj. - Wekiva
| Well 5 | Well 6 | Well 7 | Well 8 | Well 9 | Total Wells | Wekiva Proof | Well 5 Meter Adj. % 04/17/18 -0.74% 02/21/19 2.91% | Well 5 Pumped Adj. | Well 6 Meter Adj. % 04/17/18 0.70% 02/21/19 2.44% | Well 6 Pumped Adj. | Well 7 Meter Adj. % 04/17/18 -0.26% 02/21/19 0.20% | Well 7 Pumped Meter Adj. | Well 8 Meter Adj. % 04/17/18 -0.40%02/21/19 -1.83% | Well 8 Pumped Meter Adj. | Well 9 Meter Adj. % 02/21/19 -1.27% | Well 9 Pumped Meter Adj. | Total Adj. |  | Well 5 Meter Adj. % (05/12/17 -1.52%) 04/17/18 -0.74% | Well 5 Pumped Adj. | Well 6 Meter Adj. % (05/12/17 +0.99%) 04/17/18 0.70% | Well 6 Pumped Adj. | Well 7 Meter Adj. % (05/12/17 +0.62%) 04/17/18 -0.26% | Well 7 Pumped Meter Adj. | Well 8 Meter Adj. % (05/12/17 +0.84%) 04/17/18 -0.40% | Well 8 Pumped Meter Adj. | Well 9 Meter Adj. % (05/12/17 +1.19%) | Well 9 Pumped Meter Adj. | Total Adj.
2019-01-01 | 0 | 0.5849 | 0.859 | 105.539 | 1.3164 | 108.2993 | 0 | -0.74% | 0 | 0.7% | 0.0040943 | -0.26% | -0.0022334 | -0.4% | -0.42216 | 1.19% | 0.015665 | -0.40463 |  | -1.52% | -0.12427 | 0.99% | 0.082148 | 0.62% | 0.074636 | 0.84% | 0.13902 | 1.19% | -0.54886 | -0.37732
February | 0.3626 | 0.4214 | 0.621 | 93.567 | 0.95439 | 95.9264 | 0 | -0.74% & 2.91% | 0.0023793 | 0.70% & 2.44% | 0.0037845 | -0.26% & 0.2% | 0.0001604 | -0.4% & -1.83% | -2.05 | 1.19% & -1.27% | -0.0044187 | -2.0481 |  | -0.74% | -0.075521 | 0.7% | 0.077237 | -0.26% | -0.039632 | -0.4% | 0 | 1.19% | 0 | -0.037916
March | 1.5299 | 1.5757 | 2.322 | 116.476 | 4.388 | 126.2916 | 0 | 2.91% | 0.04452 | 2.44% | 0.038447 | 0.2% | 0.004644 | -1.83% | -2.1315 | -1.27% | -0.055728 | -2.0996 |  |  | -0.19979 |  | 0.15938 |  | 0.035004 |  | 0.13902 |  |  | -0.62465
April | 18.381 | 19.3316 | 27.281 | 16.55 | 43.217 | 124.7606 | 0 | 2.91% | 0.53489 | 2.44% | 0.47169 | 0.2% | 0.054562 | -1.83% | -0.30286 | -1.27% | -0.54886 | 0.20942
May | 17.8411 | 17.6227 | 25.95 | 44.781 | 41.227 | 147.4218 | 0 | 2.91% | 0.51918 | 2.44% | 0.42999 | 0.2% | 0.0519 | -1.83% | -0.81949 | -1.27% | -0.52358 | -0.34201 |  | Source Meter Error Adj. - Wekiva
June | 1.3209 | 1.3857 | 2.048 | 124.546 | 2.915 | 132.2156 | 0 | 2.91% | 0.038438 | 2.44% | 0.033811 | 0.2% | 0.004096 | -1.83% | -2.2792 | -1.27% | -0.03702 | -2.2399 |  | Well 5 Meter Adj. % 04/17/18 -0.74% 02/21/19 2.91% | Well 5 Pumped Adj. | Well 6 Meter Adj. % 04/17/18 0.70% 02/21/19 2.44% | Well 6 Pumped Adj. | Well 7 Meter Adj. % 04/17/18 -0.26% 02/21/19 0.20% | Well 7 Pumped Meter Adj. | Well 8 Meter Adj. % 04/17/18 -0.40%02/21/19 -1.83% | Well 8 Pumped Meter Adj. | Well 9 Meter Adj. % 02/21/19 -1.27% | Well 9 Pumped Meter Adj. | Total Adj.
July | 0.6756 | 0.8731 | 1.279 | 123.875 | 1.868 | 128.5707 | 0 | 2.91% | 0.01966 | 2.44% | 0.021304 | 0.2% | 0.002558 | -1.83% | -2.2669 | -1.27% | -0.023724 | -2.2471 |  | -0.74% | -0.0016569 | 0.7% | 0.0019691 | -0.26% | -0.0010816 | -0.4% | -0.27855 | 1.19% | 0.007702 | -0.27162
August | 0.2249 | 0.2274 | 0.338 | 117.156 | 0.493 | 118.4393 | 0 | 2.91% | 0.0065446 | 2.44% | 0.0055486 | 0.2% | 0.000676 | -1.83% | -2.144 | -1.27% | -0.0062611 | -2.1374 |  | 2.91% | 0.0040362 | 2.44% | 0.0018154 | 0.2% | 0.001242 | -1.83% | -1.7715 | -1.27% | -0.012121 | -1.7765
September | 1.1013 | 1.1356 | 1.681 | 116.34 | 2.432 | 122.6899 | 0 | 2.91% | 0.032048 | 2.44% | 0.027709 | 0.2% | 0.003362 | -1.83% | -2.129 | -1.27% | -0.030886 | -2.0968 |  |  | 0.0023793 |  | 0.0037845 |  | 0.0001604 |  | -2.05 |  | -0.0044187 | 0.02091
October | 1.0262 | 1.0613 | 1.531 | 115.008 | 1.827 | 120.4535 | 0 | 2.91% | 0.029862 | 2.44% | 0.025896 | 0.2% | 0.003062 | -1.83% | -2.1046 | -1.27% | -0.023203 | -2.069
November | 0.1221 | 0.1233 | 0.184 | 115.439 | 0.267 | 116.1354 | 0 | 2.91% | 0.0035531 | 2.44% | 0.0030085 | 0.2% | 0.000368 | -1.83% | -2.1125 | -1.27% | -0.0033909 | -2.109
December | 0.1875 | 0.1901 | 0.281 | 107.329 | 3.731 | 111.7186 | 0 | 2.91% | 0.0054563 | 2.44% | 0.0046384 | 0.2% | 0.000562 | -1.83% | -1.9641 | -1.27% | -0.047384 | -2.0008
Total Adjustments
January | 0.43854 |  |  |  | January | February | March | April | May | June | July | August | September | October | November | December | Total
February | -1.5706 |  |  | Mirror Lk I/C | 0.001 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0.002 | 0.092
March | -0.70423 |  |  | Org Cty I/C | [12 empty] | 0
April | 1.575
May | 1.3579
June | -0.98804
July | -1.0146
August | -1.1205
September | -0.8764
October | -0.90193
November | -0.99698
December | -1.0642
Jan
January | Wekiva Jan
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
| Well 6 | 0 | 0 | 0 | 0 | 0 | 0.0574 | 0 | 0 | 0 | 0.0583 | 0 | 0.0691 | 0.0638 | 0 | 0 | 0.0524 | 0.0455 | 0.0049 | 0.0667 | 0.0584 | 0 | 0 | 0.0533 | 0 | 0 | 0.0551 | 0 | 0 | 0 | 0 | 0 | 0.5849 |  |  | 0
| Well 7 | 0 | 0 | 0 | 0 | 0 | 0.084 | 0 | 0 | 0 | 0.085 | 0 | 0.103 | 0.094 | 0 | 0 | 0.077 | 0.067 | 0.004 | 0.098 | 0.086 | 0 | 0 | 0.079 | 0 | 0 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0.859 |  |  | 0
| Well 8 | 3.39 | 3.57 | 3.97 | 3.55 | 3.575 | 3.212 | 3.323 | 3.147 | 3.658 | 3.67 | 3.275 | 3.825 | 3.589 | 3.663 | 3.266 | 3.53 | 3.613 | 3.558 | 3.764 | 3.447 | 3.061 | 3.03 | 3.618 | 3.643 | 2.983 | 3.285 | 3.332 | 2.849 | 2.756 | 3.233 | 3.154 | 105.539 |  |  | 0
| Well 9 | 0 | 0 | 0 | 0 | 0 | 0.13164 | 0 | 0 | 0 | 0.13164 | 0 | 0.15358 | 0.14261 | 0 | 0 | 0.08776 | 0.09873 | 0.04388 | 0.15358 | 0.13164 | 0 | 0 | 0.08776 | 0.03291 | 0 | 0.12067 | 0 | 0 | 0 | 0 | 0 | 1.3164 |  |  | 0
| Total | 3.39 | 3.57 | 3.97 | 3.55 | 3.575 | 3.485 | 3.323 | 3.147 | 3.658 | 3.9449 | 3.275 | 4.1507 | 3.8894 | 3.663 | 3.266 | 3.7472 | 3.8242 | 3.6108 | 4.0823 | 3.723 | 3.061 | 3.03 | 3.8381 | 3.6759 | 2.983 | 3.5428 | 3.332 | 2.849 | 2.756 | 3.233 | 3.154 | 108.2993 | 3.4935 | 4.1507
Des Pinar Jan
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00235 |  |  | 0
| Well 1A | 1.035 | 1.855 | 1.655 | 1.336 | 1.599 | 1.598 | 1.349 | 1.141 | 1.482 | 1.651 | 1.495 | 1.652 | 1.883 | 1.658 | 1.116 | 1.494 | 1.669 | 1.721 | 1.489 | 1.767 | 1.234 | 1.518 | 1.5 | 1.548 | 1.425 | 1.712 | 1.602 | 1.548 | 1.383 | 1.136 | 1.692 | 46.943 |  |  | 0
| Well 2 | 0.068 | 0.315 | 0.405 | 0 | 0.321 | 0.321 | 0 | 0.134 | 0.317 | 0.451 | 0 | 0.398 | 0.655 | 0 | 0.144 | 0.382 | 0.397 | 0.095 | 0.433 | 0.429 | 0 | 0.023 | 0.276 | 0.275 | 0.051 | 0.334 | 0.281 | 0 | 0 | 0.26 | 0.229 | 6.994 |  |  | 0
| Well 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.259 | 0 | 0 | 0 | 0.069 | 0 | 0 | 0.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | 0 | 0 | 0 | 0.594 |  |  | 0
| Total | 1.103 | 2.17 | 2.06 | 1.336 | 1.92 | 1.919 | 1.349 | 1.275 | 1.799 | 2.106 | 1.495 | 2.05 | 2.797 | 1.658 | 1.26 | 1.876 | 2.1353 | 1.816 | 1.922 | 2.381 | 1.234 | 1.541 | 1.776 | 1.823 | 1.476 | 2.046 | 1.962 | 1.548 | 1.383 | 1.396 | 1.921 | 54.5333 | 1.7591 | 2.797
Knollwood Jan
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0 | 0 | 0 | 0 | 0.0146 | 0.0145 | 0 | 0 | 0.0345 | 0.0003 | 0 | 0 | 0.0268 | 0 | 0 | 0 | 0 | 0.0278 | 0 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0.177 |  |  | 0
| Well 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0 | 0 | 0 | 0.194 |  |  | 0
| Total | 0 | 0 | 0 | 0 | 0.0146 | 0.0145 | 0 | 0 | 0.0345 | 0.0643 | 0 | 0 | 0.0528 | 0 | 0 | 0 | 0 | 0.0838 | 0 | 0.0245 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0.048 | 0 | 0 | 0 | 0 | 0.371 | 0.011968 | 0.0838
Feb
February | Wekiva Feb
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  |  |  | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0497 | 0.0539 | 0 | 0 | 0.0554 | 0 | 0 | 0.0659 | 0.0728 | 0 | 0 | 0 | 0 |  |  |  | 0.3626 |  |  | 0
| Well 6 | 0 | 0 | 0.0544 | 0 | 0 | 0 | 0 | 0 | 0.066 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.0401 | 0.0544 | 0 | 0 | 0.0564 | 0 | 0.0657 | 0 | 0.0744 | 0 | 0 | 0 | 0 |  |  |  | 0.4214 |  |  | 0
| Well 7 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0.08 | 0 | 0 | 0.084 | 0 | 0.095 | 0 | 0.11 | 0 | 0 | 0 | 0 |  |  |  | 0.621 |  |  | 0
| Well 8 | 3.023 | 3.616 | 3.188 | 3.207 | 2.987 | 3.393 | 3.68 | 3.427 | 3.485 | 3.605 | 3.047 | 2.736 | 3.486 | 2.84 | 3.139 | 3.372 | 3.581 | 3.14 | 3.68 | 2.837 | 3.691 | 3.558 | 3.558 | 3.802 | 3.626 | 3.186 | 3.442 | 3.235 |  |  |  | 93.567 |  |  | 0
| Well 9 | 0 | 0 | 0.13164 | 0 | 0 | 0 | 0 | 0 | 0.14261 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12067 | 0.12067 | 0 | 0 | 0.13164 | 0 | 0 | 0.14261 | 0.16455 | 0 | 0 | 0 | 0 |  |  |  | 0.95439 |  |  | 0
| Total | 3.023 | 3.616 | 3.454 | 3.207 | 2.987 | 3.393 | 3.68 | 3.427 | 3.8565 | 3.605 | 3.047 | 2.746 | 3.486 | 2.84 | 3.139 | 3.6565 | 3.89 | 3.14 | 3.68 | 3.1644 | 3.691 | 3.7187 | 3.7665 | 4.2237 | 3.626 | 3.186 | 3.442 | 3.235 |  |  |  | 95.9264 | 3.4259 | 4.2237
Des Pinar Feb
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  |  |  | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0.00282 |  |  | 0
| Well 1A | 1.072 | 1.628 | 1.888 | 1.288 | 1.269 | 1.394 | 1.496 | 1.861 | 1.509 | 1.712 | 1.42 | 1.296 | 1.185 | 2.148 | 1.143 | 2.533 | 0.841 | 1.259 | 1.789 | 1.188 | 1.443 | 1.517 | 1.74 | 1.781 | 1.645 | 1.466 | 1.394 | 1.444 |  |  |  | 42.349 |  |  | 0
| Well 2 | 0 | 0.295 | 0.461 | 0 | 0.002 | 0.332 | 0.309 | 0.159 | 0.446 | 0.305 | 0 | 0 | 0.187 | 0.909 | 0.121 | 0.304 | 0.489 | 0.005 | 0.042 | 0.259 | 0.356 | 0.134 | 0.464 | 0.52 | 0.061 | 0.196 | 0.298 | 0.231 |  |  |  | 6.885 |  |  | 0
| Well 2A | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0.236 | 0 | 0 | 0 | 0.289 | 0 | 0.043 | 0.087 | 0 | 0 | 0 | 0.073 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 |  |  |  | 1.188 |  |  | 0
| Total | 1.072 | 1.923 | 2.349 | 1.288 | 1.2835 | 1.726 | 1.805 | 2.02 | 1.955 | 2.253 | 1.42 | 1.296 | 1.372 | 3.346 | 1.264 | 2.88 | 1.417 | 1.264 | 1.831 | 1.447 | 1.8723 | 1.651 | 2.204 | 2.751 | 1.706 | 1.662 | 1.692 | 1.675 |  |  |  | 50.4248 | 1.8009 | 3.346
Knollwood Feb
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  |  |  | Total | Avg | Max | Proof
| Well 3 | 0 | 0 | 0.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0257 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0.0421 |  |  | 0
| Well 4 | 0 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0.076 |  |  | 0
| Total | 0 | 0 | 0.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0.0257 | 0 | 0.023 | 0 | 0 | 0 | 0.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0.1181 | 0.0042179 | 0.0331
Mar
March | Wekiva March
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0 | 0.0574 | 0.0639 | 0 | 0 | 0.053 | 0.0559 | 0 | 0 | 0.1596 | 0 | 0 | 0.0803 | 0.0935 | 0 | 0.1023 | 0.1111 | 0 | 0 | 0.0532 | 0.0649 | 0.0133 | 0.0704 | 0.115 | 0 | 0 | 0.0854 | 0.0891 | 0 | 0.1099 | 0.1517 | 1.5299 |  |  | 0
| Well 6 | 0 | 0.0582 | 0.0667 | 0 | 0 | 0.0518 | 0.0564 | 0 | 0.0657 | 0.0981 | 0 | 0 | 0.0825 | 0.0963 | 0 | 0.1206 | 0.101 | 0 | 0 | 0.0593 | 0.0083 | 0.0644 | 0.0741 | 0.1193 | 0 | 0 | 0.0878 | 0.0918 | 0 | 0.1191 | 0.1543 | 1.5757 |  |  | 0
| Well 7 | 0 | 0.086 | 0.096 | 0 | 0 | 0.079 | 0.083 | 0 | 0.097 | 0.143 | 0 | 0 | 0.124 | 0.142 | 0 | 0.152 | 0.175 | 0 | 0 | 0.085 | 0.093 | 0.017 | 0.108 | 0.176 | 0 | 0 | 0.129 | 0.135 | 0 | 0.136 | 0.266 | 2.322 |  |  | 0
| Well 8 | 3.087 | 3.185 | 3.857 | 3.776 | 3.144 | 3.329 | 3.383 | 3.799 | 4.059 | 3.521 | 4.32 | 3.476 | 3.601 | 3.851 | 3.992 | 3.677 | 4.108 | 3.977 | 3.262 | 3.151 | 3.67 | 3.351 | 4.404 | 3.66 | 4.897 | 3.808 | 4.085 | 3.741 | 4.127 | 4.23 | 3.948 | 116.476 |  |  | 0
| Well 9 | 0 | 0.126 | 0.14 | 0 | 0 | 0.116 | 0.122 | 0 | 0.143 | 0.211 | 0 | 0 | 0.178 | 0.207 | 0 | 0 | 0.474 | 0 | 0 | 0.128 | 0.132 | 0.113 | 0.073 | 0.255 | 0 | 0 | 0.189 | 0.198 | 0 | 0.756 | 0.827 | 4.388 |  |  | 0
| Total | 3.087 | 3.5126 | 4.2236 | 3.776 | 3.144 | 3.6288 | 3.7003 | 3.799 | 4.3647 | 4.1327 | 4.32 | 3.476 | 4.0658 | 4.3898 | 3.992 | 4.0519 | 4.9691 | 3.977 | 3.262 | 3.4765 | 3.9682 | 3.5587 | 4.7295 | 4.3253 | 4.897 | 3.808 | 4.5762 | 4.2549 | 4.127 | 5.351 | 5.347 | 126.2916 | 4.0739 | 5.351
Des Pinar March
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00018 |  |  | 0
| Well 1A | 1.6 | 1.314 | 2.074 | 1.369 | 1.103 | 1.733 | 1.48 | 1.266 | 1.77 | 1.978 | 1.711 | 1.726 | 1.718 | 1.168 | 1.688 | 1.763 | 2.217 | 1.577 | 1.341 | 1.42 | 1.478 | 1.706 | 1.458 | 1.813 | 1.216 | 1.828 | 1.579 | 1.72 | 1.38 | 1.581 | 2.279 | 50.054 |  |  | 0
| Well 2 | 0 | 0.344 | 0.482 | 0 | 0.066 | 0.394 | 0.358 | 0 | 0.478 | 0.699 | 0.346 | 0.223 | 0.462 | 0.314 | 0.316 | 0.568 | 0.86 | 0.124 | 0.165 | 0.352 | 0.334 | 0 | 0.403 | 0.5 | 0 | 0 | 0.395 | 0.277 | 0 | 0.392 | 0.619 | 9.471 |  |  | 0
| Well 2A | 0 | 0.061 | 0.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0.508 | 0 | 0 | 0.27 | 0.227 | 0 | 0 | 0.526 | 0 | 0 | 0.002 | 0.135 | 0 | 0 | 0.519 | 0 | 0 | 0.191 | 0.219 | 0 | 0.283 | 0.254 | 3.386 |  |  | 0
| Total | 1.6 | 1.719 | 2.747 | 1.369 | 1.169 | 2.127 | 1.838 | 1.266 | 2.248 | 3.185 | 2.057 | 1.949 | 2.45 | 1.709 | 2.004 | 2.331 | 3.603 | 1.701 | 1.506 | 1.7742 | 1.947 | 1.706 | 1.861 | 2.832 | 1.216 | 1.828 | 2.165 | 2.216 | 1.38 | 2.256 | 3.152 | 62.9112 | 2.0294 | 3.603
Knollwood March
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0148 | 0.0606 | 0.0563 | 0 | 0 | 0.0984 | 0 | 0.0657 | 0.2147 | 0.5777 |  |  | 0
| Well 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0.225 | 0.091 | 0 | 0 | 0 | 0.139 | 0 | 0 | 0.511 |  |  | 0
| Total | 0 | 0.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0.0148 | 0.2856 | 0.1473 | 0 | 0 | 0.0984 | 0.139 | 0.0657 | 0.2147 | 1.0887 | 0.035119 | 0.2856
April
April | Wekiva April
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0.0863 | 0.094 | 0.6734 | 0.673 | 0.6475 | 0.7155 | 0.4962 | 0.592 | 0.6799 | 0.7082 | 0.7281 | 0.7859 | 0.6944 | 0.6011 | 0.6582 | 0.8356 | 0.6198 | 0.7119 | 0.5461 | 0.7008 | 0.5797 | 0.7873 | 0.8457 | 0.6941 | 0.6363 | 0.9623 | 0.9135 | 0.7142 |  | 18.381 |  |  | 0
| Well 6 | 0 | 0 | 0.0891 | 0.0969 | 0.6772 | 0.6304 | 0.7195 | 0.7306 | 0.4972 | 0.6016 | 0.7017 | 0.7131 | 0.7043 | 0.799 | 0.7859 | 0.5513 | 0.6529 | 0.9465 | 0.8199 | 0.6049 | 0.4675 | 0.7092 | 0.5709 | 0.8035 | 0.8693 | 0.6968 | 0.6857 | 0.9521 | 0.9376 | 1.317 |  | 19.3316 |  |  | 0
| Well 7 | 0 | 0 | 0.124 | 0.15 | 0.976 | 0.93 | 1.011 | 1.05 | 0.719 | 0.868 | 1.017 | 1.075 | 1.033 | 1.23 | 1.043 | 0.812 | 1.128 | 1.21 | 0.901 | 1.09 | 0.774 | 1.035 | 0.835 | 1.178 | 1.271 | 1.015 | 1.005 | 1.386 | 1.361 | 1.054 |  | 27.281 |  |  | 0
| Well 8 | 5.646 | 3.31 | 3.45 | 3.966 | 0.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16.55 |  |  | 0
| Well 9 | 0 | 0 | -0.708 | 1.109 | 1.607 | 1.581 | 1.555 | 1.706 | 1.185 | 1.373 | 1.616 | 1.778 | 1.557 | 1.703 | 1.889 | 1.32 | 1.634 | 1.917 | 1.468 | 1.459 | 1.501 | 1.641 | 1.378 | 1.812 | 1.968 | 1.632 | 1.181 | 2.531 | 2.132 | 1.692 |  | 43.217 |  |  | 0
| Total | 5.646 | 3.31 | 3.0414 | 5.4159 | 4.1116 | 3.8144 | 3.933 | 4.2021 | 2.8974 | 3.4346 | 4.0146 | 4.2743 | 4.0224 | 4.5179 | 4.4123 | 3.2844 | 4.0731 | 4.9091 | 3.8087 | 3.8658 | 3.2886 | 4.086 | 3.3636 | 4.5808 | 4.954 | 4.0379 | 3.508 | 5.8314 | 5.3441 | 4.7772 |  | 124.7606 | 4.1587 | 5.8314
Des Pinar April
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0002 |  |  | 0
| Well 1A | 1.507 | 1.696 | 1.453 | 1.641 | 1.673 | 1.358 | 1.908 | 1.327 | 1.595 | 1.437 | 1.718 | 1.348 | 1.783 | 1.769 | 1.094 | 1.459 | 1.984 | 1.666 | 1.396 | 1.749 | 1.9 | 1.489 | 1.5 | 1.731 | 1.701 | 1.662 | 1.614 | 2.19 | 1.711 | 1.766 |  | 48.825 |  |  | 0
| Well 2 | 0 | 0 | 0.384 | 0.353 | 0 | 0.309 | 0.3 | 0 | 0 | 0.315 | 0.299 | 0 | 0.401 | 0.461 | 0.001 | 0 | 0.423 | 0.358 | 0 | 0.26 | 0.335 | 0 | 0.158 | 0.443 | 0.43 | 0.142 | 0.531 | 0.625 | 0.546 | 0.302 |  | 7.376 |  |  | 0
| Well 2A | 0 | 0 | 0.261 | 0.197 | 0 | 0.288 | 0.121 | 0 | 0 | 0.184 | 0.174 | 0.001 | 0 | 0.574 | 0.003 | 0 | 0.25 | 0.284 | 0 | 0 | 0.335 | 0 | 0 | 0.318 | 0.245 | 0 | 0.14 | 0.717 | 0 | 0.111 |  | 4.203 |  |  | 0
| Total | 1.507 | 1.696 | 2.098 | 2.191 | 1.673 | 1.955 | 2.329 | 1.327 | 1.595 | 1.936 | 2.191 | 1.349 | 2.184 | 2.804 | 1.0982 | 1.459 | 2.657 | 2.308 | 1.396 | 2.009 | 2.57 | 1.489 | 1.658 | 2.492 | 2.376 | 1.804 | 2.285 | 3.532 | 2.257 | 2.179 |  | 60.4042 | 2.0135 | 3.532
Knollwood April
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 3 | 0.0886 | 0 | 0.0179 | 0.0528 | 0.0176 | 0.0168 | 0.0609 | 0 | 0.0146 | 0.0245 | 0.0427 | 0 | 0.013 | 0.0392 | 0.0247 | 0.0003 | 0.0405 | 0.0143 | 0.0273 | 0.0064 | 0.0113 | 0 | 0.0255 | 0.0425 | 0.0124 | 0.0364 | 0.0125 | 0.0666 | 0.0417 | 0.0206 |  | 0.7716 |  |  | 0
| Well 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096 | 0.029 | 0.023 | 0.024 | 0.029 | 0.022 | 0 | 0.134 | 0.001 | 0.025 | 0.08 | 0.049 | 0 | 0 | 0.049 | 0.022 | 0.022 | 0 | 0.132 | 0.029 | 0 | 0.13 | 0.027 | 0.051 |  | 0.974 |  |  | 0
| Total | 0.0886 | 0 | 0.0179 | 0.0528 | 0.0176 | 0.0168 | 0.1569 | 0.029 | 0.0376 | 0.0485 | 0.0717 | 0.022 | 0.013 | 0.1732 | 0.0257 | 0.0253 | 0.1205 | 0.0633 | 0.0273 | 0.0064 | 0.0603 | 0.022 | 0.0475 | 0.0425 | 0.1444 | 0.0654 | 0.0125 | 0.1966 | 0.0687 | 0.0716 |  | 1.7456 | 0.058187 | 0.1966
May
May | Wekiva May
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0.7751 | 0.8829 | 0.7277 | 0.7787 | 0.7719 | 0.7874 | 0.5526 | 0.7268 | 0.9741 | 0.6442 | 0.9277 | 0.6794 | 0.7079 | 0.5084 | 0.6356 | 0.8626 | 0.7007 | 0.7782 | 0.8058 | 0.8705 | 0.7713 | 0.8373 | 0.3875 | 0 | 0.1389 | 0.1719 | 0.0927 | 0 | 0.0906 | 0.2 | 0.0527 | 17.8411 |  |  | 0
| Well 6 | 0.1855 | 0.9182 | 0.7396 | 0.7909 | 0.7967 | 0.8154 | 0.5443 | 0.7357 | 1.0039 | 0.6529 | 1.1105 | 0.5467 | 0.7138 | 0.4988 | 0.6445 | 0.8905 | 0.7038 | 0.7862 | 0.8483 | 0.8973 | 0.7261 | 0.8516 | 0.4155 | 0 | 0.0826 | 0.2535 | 0.1702 | 0 | 0.0314 | 0.2133 | 0.055 | 17.6227 |  |  | 0
| Well 7 | 1.149 | 1.331 | 1.068 | 1.148 | 1.153 | 0.707 | 0.731 | 1.06 | 1.441 | 0.953 | 1.449 | 0.95 | 1.026 | 0.719 | 0.944 | 1.276 | 1.017 | 1.686 | 0.686 | 1.294 | 1.131 | 1.275 | 0.561 | 0 | 0.194 | 0.311 | 0.222 | 0 | 0.078 | 0.313 | 0.077 | 25.95 |  |  | 0
| Well 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.805 | 5.148 | 4.687 | 4.673 | 5.848 | 4.451 | 5.372 | 5.353 | 5.444 | 44.781 |  |  | 0
| Well 9 | 1.829 | 2.051 | 1.715 | 1.794 | 1.803 | 1.813 | 1.273 | 1.554 | 2.302 | 1.497 | 2.315 | 1.431 | 1.662 | 1.199 | 1.474 | 1.875 | 1.642 | 1.803 | 1.877 | 2.034 | 1.729 | 2.009 | 0.875 | 0 | 0.152 | 0.537 | 0.264 | 0 | 0.146 | 0.448 | 0.124 | 41.227 |  |  | 0
| Total | 3.9386 | 5.1831 | 4.2503 | 4.5116 | 4.5246 | 4.1228 | 3.1009 | 4.0765 | 5.721 | 3.7471 | 5.8022 | 3.6071 | 4.1097 | 2.9252 | 3.6981 | 4.9041 | 4.0635 | 5.0534 | 4.2171 | 5.0958 | 4.3574 | 4.9729 | 6.044 | 5.148 | 5.2545 | 5.9464 | 6.5969 | 4.451 | 5.718 | 6.5273 | 5.7527 | 147.4218 | 4.7555 | 6.5969
Des Pinar May
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-05 | 0 | 0.00038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0004 |  |  | 0
| Well 1A | 1.405 | 2.059 | 1.482 | 1.791 | 2.089 | 1.2 | 1.581 | 1.419 | 1.7 | 1.465 | 1.145 | 2.014 | 1.265 | 1.172 | 1.321 | 1.367 | 1.15 | 1.57 | 2.014 | 1.542 | 1.478 | 1.674 | 1.686 | 1.894 | 1.482 | 2.268 | 1.303 | 2.172 | 1.858 | 1.901 | 1.418 | 49.885 |  |  | 0
| Well 2 | 0.338 | 0.761 | 0.196 | 0.491 | 0.614 | 0 | 0.225 | 0.46 | 0.531 | 0.215 | 0.471 | 0.62 | 0.114 | 0.179 | 0.377 | 0.173 | 0.512 | 0.504 | 0.719 | 0.448 | 0.511 | 0.832 | 0.871 | 0.784 | 0.753 | 1.399 | 0.69 | 1.342 | 1.086 | 1.42 | 1.122 | 18.758 |  |  | 0
| Well 2A | 0.51 | 0.279 | 0 | 0.478 | 0.371 | 0 | 0 | 0.332 | 0.344 | 0 | 0 | 0.692 | 0 | 0 | 0.231 | 0.216 | 0 | 0 | 0.751 | 0 | 0.002 | 0.526 | 0.351 | 0 | 0 | 1.036 | 0 | 0.122 | 0.432 | 0.724 | 0.199 | 7.596 |  |  | 0
| Total | 2.253 | 3.099 | 1.678 | 2.76 | 3.074 | 1.2 | 1.806 | 2.211 | 2.575 | 1.68 | 1.616 | 3.326 | 1.379 | 1.351 | 1.929 | 1.756 | 1.662 | 2.074 | 3.484 | 1.99 | 1.9914 | 3.032 | 2.908 | 2.678 | 2.235 | 4.703 | 1.993 | 3.636 | 3.376 | 4.045 | 2.739 | 76.2394 | 2.4593 | 4.703
Knollwood May
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0.0446 | 0.0645 | 0.0243 | 0.0127 | 0.0145 | 0.001 | 0.0288 | 0.0255 | 0.0113 | 0.022 | 0.0112 | 0.0122 | 0 | 0 | 0.0202 | 0.0115 | 0.0333 | 0.0114 | 0.0369 | 0.0264 | 0 | 0.0369 | 0.0402 | 0 | 0.0142 | 0.0377 | 0 | 0.0386 | 0.0382 | 0.0195 | 0.0127 | 0.6503 |  |  | 0
| Well 4 | 0.104 | 0.083 | 0 | 0.056 | 0.08 | 0.026 | 0 | 0.131 | 0.086 | 0 | 0 | 0.122 | 0 | 0.024 | 0.061 | 0.059 | 0 | 0 | 0.147 | 0.028 | 0.03 | 0.087 | 0.064 | 0 | 0 | 0.311 | 0 | 0.029 | 0.16 | 0.192 | 0.043 | 1.923 |  |  | 0
| Total | 0.1486 | 0.1475 | 0.0243 | 0.0687 | 0.0945 | 0.027 | 0.0288 | 0.1565 | 0.0973 | 0.022 | 0.0112 | 0.1342 | 0 | 0.024 | 0.0812 | 0.0705 | 0.0333 | 0.0114 | 0.1839 | 0.0544 | 0.03 | 0.1239 | 0.1042 | 0 | 0.0142 | 0.3487 | 0 | 0.0676 | 0.1982 | 0.2115 | 0.0557 | 2.5733 | 0.08301 | 0.3487
June
June | Wekiva June
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 5 | 0.2109 | 0.1485 | 0.0433 | 0 | 0.181 | 0.1187 | 0.003 | 0 | 0.0699 | 0 | 0 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0.0944 | 0 | 0 | 0.0713 | 0.1054 | 0 | 0.1056 | 0.1057 |  | 1.3209 |  |  | 0
| Well 6 | 0.2092 | 0.1794 | 0.0445 | 0 | 0.1995 | 0.1203 | 0 | 0 | 0.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0637 | 0.0964 | 0 | 0 | 0.0722 | 0.1081 | 0 | 0.1086 | 0.1087 |  | 1.3857 |  |  | 0
| Well 7 | 0.308 | 0.268 | 0.061 | 0 | 0.297 | 0.174 | 0 | 0 | 0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0.138 | 0 | 0 | 0.111 | 0.161 | 0 | 0.162 | 0.162 |  | 2.048 |  |  | 0
| Well 8 | 5.765 | 4.465 | 5.322 | 4.708 | 5.19 | 4.608 | 3.934 | 3.77 | 4.237 | 3.608 | 3.369 | 4.001 | 3.808 | 3.544 | 3.323 | 4.437 | 3.75 | 3.178 | 3.716 | 4.119 | 3.131 | 4.396 | 3.655 | 0 | 8.702 | 4.344 | 4.27 | 4.398 | 4.699 | 4.099 |  | 124.546 |  |  | 0
| Well 9 | 0.434 | 0.359 | 0.103 | 0 | 0.395 | 0.271 | 0 | 0 | 0.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0.206 | 0 | 0 | 0.15 | 0.236 | 0 | 0.23 | 0.231 |  | 2.915 |  |  | 0
| Total | 6.9271 | 5.4199 | 5.5738 | 4.708 | 6.2625 | 5.292 | 3.937 | 3.77 | 4.655 | 3.608 | 3.369 | 4.064 | 3.808 | 3.544 | 3.323 | 4.437 | 3.75 | 3.178 | 3.716 | 4.119 | 3.131 | 4.6929 | 4.1898 | 0 | 8.702 | 4.7485 | 4.8805 | 4.398 | 5.3052 | 4.7064 |  | 132.2156 | 4.4072 | 8.702
Des Pinar June
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0004 |  |  | 0
| Well 1A | 1.368 | 2.08 | 1.488 | 1.035 | 1.204 | 1.327 | 0.793 | 0.796 | 1.111 | 0.72 | 0.73 | 0.64 | 1.032 | 0.587 | 0.836 | 1.075 | 0.662 | 0.572 | 0.811 | 0.857 | 0.603 | 1.056 | 1.298 | 0.829 | 1.182 | 1.109 | 1.274 | 1.179 | 1.166 | 1.498 |  | 30.918 |  |  | 0
| Well 2 | 1.075 | 0.641 | 2.168 | 0.813 | 0.944 | 1.04 | 0.743 | 0.855 | 0.866 | 0.555 | 0.564 | 0.507 | 0.796 | 0.452 | 0.652 | 0.84 | 0.51 | 0.417 | 0.65 | 0.657 | 0.465 | 0.825 | 1.014 | 0.646 | 0.922 | 0.866 | 0.998 | 0.928 | 0.915 | 1.176 |  | 24.5 |  |  | 0
| Well 2A | 0 | 1.185 | 0.074 | 0.13 | 0.357 | 0.433 | 0 | 0 | 0.224 | 0 | 0 | 0.138 | 0 | 0 | 0 | 0.127 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.347 | 0 | 0 | 0.296 | 0.356 | 0 | 0.349 | 0.407 |  | 4.428 |  |  | 0
| Total | 2.443 | 3.906 | 3.73 | 1.978 | 2.505 | 2.8 | 1.536 | 1.651 | 2.201 | 1.275 | 1.294 | 1.285 | 1.828 | 1.039 | 1.488 | 2.042 | 1.172 | 0.989 | 1.4664 | 1.514 | 1.068 | 1.881 | 2.659 | 1.475 | 2.104 | 2.271 | 2.628 | 2.107 | 2.43 | 3.081 |  | 59.8464 | 1.9949 | 3.906
Knollwood June
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 3 | 0.0118 | 0.0731 | 0.0122 | 0.0437 | 0.0154 | 0.0264 | 0.012 | 0.0115 | 0.0124 | 0 | 0 | 0 | 0 | 0.0295 | 0 | 0.0139 | 0 | 0 | 0.0004 | 0 | 0.0326 | 0.0106 | 0.0137 | 0.0348 | 0 | 0.0475 | 0.0404 | 0 | 0.0396 | 0.0117 |  | 0.4932 |  |  | 0
| Well 4 | 0 | 0.27 | 0.069 | 0.028 | 0.181 | 0.111 | 0.016 | 0 | 0.078 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0.02 | 0.002 | 0 | 0 | 0 | 0.145 | 0 | 0.029 | 0.109 | 0.01 | 0.026 | 0 | 0.2 |  | 1.374 |  |  | 0
| Total | 0.0118 | 0.3431 | 0.0812 | 0.0717 | 0.1964 | 0.1374 | 0.028 | 0.0115 | 0.0904 | 0 | 0.03 | 0 | 0 | 0.0295 | 0 | 0.0639 | 0 | 0.02 | 0.0024 | 0 | 0.0326 | 0.0106 | 0.1587 | 0.0348 | 0.029 | 0.1565 | 0.0504 | 0.026 | 0.0396 | 0.2117 |  | 1.8672 | 0.06224 | 0.3431
July
July | Wekiva July
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0.1603 | 0.0799 | 0.0798 | 0 | 0 | 0 | 0 | 0.0521 | 0.0799 | 0.0012 | 0 | 0.0777 | 0 | 0 | 0.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6756 |  |  | 0
| Well 6 | 0 | 0 | 0.1719 | 0.1635 | 0 | 0 | 0 | 0 | 0 | 0.0551 | 0.0788 | 0 | 0 | 0.0792 | 0 | 0 | 0.1513 | 0 | 0 | 0 | 0.1032 | 0 | 0 | 0 | 0.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8731 |  |  | 0
| Well 7 | 0 | 0 | 0.258 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0.084 | 0.115 | 0 | 0 | 0.117 | 0 | 0 | 0.224 | 0 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 1.279 |  |  | 0
| Well 8 | 4.706 | 4.161 | 4.617 | 4.609 | 2.449 | 6.145 | 3.706 | 3.705 | 3.55 | 3.96 | 3.278 | 4.52 | 3.984 | 4.163 | 0.67 | 7.523 | 4.512 | 4.008 | 3.707 | 4.112 | 4.039 | 3.741 | 3.652 | 4.256 | 3.672 | 3.558 | 4.043 | 3.609 | 4.174 | 3.314 | 3.732 | 123.875 |  |  | 0
| Well 9 | 0 | 0 | 0.347 | 0.356 | 0 | 0 | 0 | 0 | 0 | 0.106 | 0.174 | 0.009 | 0 | 0.169 | 0 | 0 | 0.318 | 0 | 0 | 0 | 0.231 | 0 | 0 | 0 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 1.868 |  |  | 0
| Total | 4.706 | 4.161 | 5.5542 | 5.4484 | 2.5288 | 6.145 | 3.706 | 3.705 | 3.55 | 4.2572 | 3.7257 | 4.5302 | 3.984 | 4.6059 | 0.67 | 7.523 | 5.35 | 4.008 | 3.707 | 4.112 | 4.5162 | 3.741 | 3.652 | 4.256 | 3.9981 | 3.558 | 4.043 | 3.609 | 4.174 | 3.314 | 3.732 | 128.5707 | 4.1474 | 7.523
Des Pinar July
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00025 |  |  | 0
| Well 1A | 1.209 | 1.37 | 1.375 | 1.368 | 1.188 | 1.223 | 1.107 | 0.766 | 0.806 | 0.969 | 0.992 | 0.79 | 0 | 2.158 | 0.988 | 0.964 | 1.28 | 0.719 | 1.071 | 0.794 | 1.463 | 0.799 | 0.776 | 1.171 | 0.927 | 0.665 | 0.868 | 1.179 | 0.548 | 0 | 0 | 29.533 |  |  | 0
| Well 2 | 0.955 | 1.083 | 1.081 | 1.075 | 0.934 | 0.956 | 0.863 | 0.596 | 0.624 | 0.756 | 0.773 | 0.616 | 0.752 | 0.927 | 0.765 | 0.751 | 0.996 | 0.562 | 0.829 | 0.618 | 1.141 | 0.614 | 0.591 | 0.921 | 0.724 | 0.513 | 0.671 | 0.92 | 0.415 | 0.783 | 1.047 | 24.852 |  |  | 0
| Well 2A | 0 | 0 | 0.358 | 0.314 | 0 | 0.159 | 0.16 | 0 | 0 | 0.172 | 0.137 | 0 | 0 | 0.281 | 0 | 0.002 | 0.337 | 0.121 | 0 | 0.077 | 0.355 | 0 | 0 | 0.106 | 0.095 | 0 | 0.045 | 0.319 | 0 | 0.606 | 0.935 | 4.579 |  |  | 0
| Total | 2.164 | 2.453 | 2.814 | 2.757 | 2.122 | 2.338 | 2.13 | 1.362 | 1.43 | 1.897 | 1.902 | 1.406 | 0.752 | 3.366 | 1.753 | 1.7172 | 2.613 | 1.402 | 1.9 | 1.489 | 2.959 | 1.413 | 1.367 | 2.198 | 1.7461 | 1.178 | 1.584 | 2.418 | 0.963 | 1.389 | 1.982 | 58.9642 | 1.9021 | 3.366
Knollwood July
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0.031 | 0.0355 | 0 | 0.0492 | 0.0264 | 0.0132 | 0.029 | 0 | 0.0175 | 0.012 | 0.016 | 0 | 0.0155 | 0.0113 | 0.0283 | 0 | 0.0554 | 0.0003 | 0.0297 | 0.0109 | 0.0199 | 0.0008 | 0 | 0.0161 | 0.008 | 0 | 0.0171 | 0.0305 | 0.0017 | 0.0187 | 0.0115 | 0.5055 |  |  | 0
| Well 4 | 0.022 | 0 | 0.22 | 0.162 | 0.09 | 0 | 0.021 | 0 | 0.018 | 0.054 | 0 | 0.054 | 0 | 0.109 | 0 | 0.029 | 0.158 | 0.033 | 0 | 0.064 | 0.132 | 0.003 | 0 | 0.083 | 0.024 | 0.029 | 0 | 0.059 | 0.006 | 0.024 | 0.08 | 1.474 |  |  | 0
| Total | 0.053 | 0.0355 | 0.22 | 0.2112 | 0.1164 | 0.0132 | 0.05 | 0 | 0.0355 | 0.066 | 0.016 | 0.054 | 0.0155 | 0.1203 | 0.0283 | 0.029 | 0.2134 | 0.0333 | 0.0297 | 0.0749 | 0.1519 | 0.0038 | 0 | 0.0991 | 0.032 | 0.029 | 0.0171 | 0.0895 | 0.0077 | 0.0427 | 0.0915 | 1.9795 | 0.063855 | 0.22
Aug
August | Wekiva Aug
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1418 | 0 | 0 | 0.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2249 |  |  | 0
| Well 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1431 | 0 | 0 | 0.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2274 |  |  | 0
| Well 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.213 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0.338 |  |  | 0
| Well 8 | 4.158 | 3.534 | 3.188 | 3.962 | 3.582 | 3.447 | 3.852 | 3.953 | 3.753 | 3.817 | 4.079 | 3.919 | 3.153 | 3.708 | 3.858 | 3.368 | 3.389 | 4.243 | 4.109 | 3.345 | 3.69 | 4.477 | 3.821 | 4.305 | 4.932 | 3.995 | 2.792 | 4.185 | 3.707 | 3.385 | 3.45 | 117.156 |  |  | 0
| Well 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.311 | 0 | 0 | 0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.493 |  |  | 0
| Total | 4.158 | 3.534 | 3.188 | 3.962 | 3.582 | 3.447 | 3.852 | 3.953 | 3.753 | 3.817 | 4.079 | 3.919 | 3.153 | 3.708 | 3.858 | 3.368 | 3.389 | 4.243 | 4.109 | 3.345 | 3.69 | 5.2859 | 3.821 | 4.305 | 5.4064 | 3.995 | 2.792 | 4.185 | 3.707 | 3.385 | 3.45 | 118.4393 | 3.8206 | 5.4064
Des Pinar Aug
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00025 | 0 | 5e-05 | 0 | 0 | 0 | 0 | 0 | 0.00017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00047 |  |  | 0
| Well 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.997 | 0.853 | 0.965 | 0.483 | 0.838 | 0.103 | 0.657 | 0.832 | 0.734 | 1.08 | 0.703 | 0.901 | 0.766 | 0.876 | 0.88 | 0.968 | 0.98 | 0.755 | 0.867 | 0.884 | 0.643 | 0.715 | 17.48 |  |  | 0
| Well 2 | 0.967 | 0.529 | 0.785 | 1.052 | 0.734 | 0.718 | 0.77 | 1.088 | 0.643 | 0.707 | 0.675 | 0.752 | 0.377 | 0.656 | 1.108 | 0.5 | 0 | 1.227 | 0.84 | 0.573 | 0.68 | 0.603 | 0.675 | 0.699 | 0.757 | 0.771 | 0.588 | 0.68 | 0.694 | 0.503 | 0.562 | 21.913 |  |  | 0
| Well 2A | 0.916 | 0.485 | 0.708 | 0.945 | 0.665 | 0.681 | 0.711 | 0.983 | 0.591 | 0 | 0.247 | 0 | 0 | 0 | 0.379 | 0 | 0 | 0 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0.393 | 0 | 0 | 0.114 | 0 | 0 | 0 | 8.03 |  |  | 0
| Total | 1.883 | 1.014 | 1.493 | 1.997 | 1.399 | 1.399 | 1.481 | 2.071 | 1.234 | 1.704 | 1.775 | 1.717 | 0.86025 | 1.494 | 1.59 | 1.157 | 0.832 | 1.961 | 2.132 | 1.276 | 1.5812 | 1.369 | 1.551 | 1.579 | 2.118 | 1.751 | 1.343 | 1.661 | 1.578 | 1.146 | 1.277 | 47.4235 | 1.5298 | 2.132
Knollwood Aug
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0 | 0.0159 | 0.0077 | 0 | 0.0001 | 0.0111 | 0.0372 | 0 | 0.0411 | 0.0135 | 0.0112 | 0 | 0.0158 | 0 | 0.0016 | 0 | 0.0207 | 0.0012 | 0.0206 | 0.0303 | 0 | 0.0564 | 0.0137 | 0 | 0.0111 | 0.0453 | 0 | 0.0126 | 0.0025 | 0.0161 | 0 | 0.3857 |  |  | 0
| Well 4 | 0 | 0 | 0 | 0.024 | 0 | 0.017 | 0.019 | 0.028 | 0 | 0 | 0.08 | 0.029 | 0.037 | 0 | 0.016 | 0.147 | 0 | 0 | 0.004 | 0 | 0 | 0.003 | 0 | 0 | 0.139 | 0.027 | 0 | 0.046 | 0.009 | 0.024 | 0 | 0.649 |  |  | 0
| Total | 0 | 0.0159 | 0.0077 | 0.024 | 0.0001 | 0.0281 | 0.0562 | 0.028 | 0.0411 | 0.0135 | 0.0912 | 0.029 | 0.0528 | 0 | 0.0176 | 0.147 | 0.0207 | 0.0012 | 0.0246 | 0.0303 | 0 | 0.0594 | 0.0137 | 0 | 0.1501 | 0.0723 | 0 | 0.0586 | 0.0115 | 0.0401 | 0 | 1.0347 | 0.033377 | 0.1501
Sept
Sept | Wekiva September
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1191 | 0.1078 | 0 | 0 | 0 | 0 | 0.001 | 0.107 | 0.0787 | 0 | 0.0702 | 0.0982 | 0 | 0 | 0.1393 | 0.1339 | 0 | 0.1189 | 0.1272 | 0 |  | 1.1013 |  |  | 0
| Well 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1231 | 0.1137 | 0 | 0 | 0 | 0 | 0 | 0.1087 | 0.082 | 0 | 0.0679 | 0.1006 | 0 | 0 | 0.145 | 0.1388 | 0 | 0.1224 | 0.1334 | 0 |  | 1.1356 |  |  | 0
| Well 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.181 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0.158 | 0.125 | 0 | 0.098 | 0.149 | 0 | 0 | 0.215 | 0.205 | 0 | 0.181 | 0.197 | 0 |  | 1.681 |  |  | 0
| Well 8 | 3.486 | 3.23 | 2.763 | 3.475 | 3.293 | 3.229 | 3.701 | 4.153 | 4.621 | 3.917 | 4.267 | 4.103 | 3.733 | 4.063 | 3.575 | 3.348 | 3.476 | 4.001 | 4.097 | 3.878 | 3.785 | 3.994 | 3.945 | 3.943 | 4.133 | 4.444 | 4.374 | 4.911 | 3.933 | 4.469 |  | 116.34 |  |  | 0
| Well 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.264 | 0.232 | 0 | 0 | 0 | 0 | 0 | 0.238 | 0.173 | 0 | 0.161 | 0.217 | 0 | 0 | 0.308 | 0.295 | 0 | 0.261 | 0.283 | 0 |  | 2.432 |  |  | 0
| Total | 3.486 | 3.23 | 2.763 | 3.475 | 3.293 | 3.229 | 3.701 | 4.153 | 4.621 | 3.917 | 4.9542 | 4.7285 | 3.733 | 4.063 | 3.575 | 3.348 | 3.477 | 4.6127 | 4.5557 | 3.878 | 4.1821 | 4.5588 | 3.945 | 3.943 | 4.9403 | 5.2167 | 4.374 | 5.5943 | 4.6736 | 4.469 |  | 122.6899 | 4.0897 | 5.5943
Des Pinar September
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0018 |  |  | 0
| Well 1A | 0.941 | 0.556 | 0.689 | 0.785 | 0.81 | 0.605 | 0.831 | 1.145 | 1.145 | 1.098 | 1.262 | 1.264 | 0.774 | 0.987 | 1.097 | 0.828 | 0.778 | 1.211 | 0.955 | 1.101 | 0.958 | 1.397 | 1.245 | 0.903 | 1.358 | 1.44 | 1.387 | 1.204 | 1.428 | 1.35 |  | 31.532 |  |  | 0
| Well 2 | 1.007 | 0.081 | 0.624 | 0.611 | 0.63 | 0.472 | 0.656 | 0.995 | 0.801 | 0.866 | 0.988 | 0.992 | 0.611 | 0.779 | 0.855 | 0.647 | 0.612 | 0.95 | 0.768 | 0.765 | 0.753 | 1.098 | 0.902 | 0.712 | 1.051 | 1.153 | 1.095 | 0.952 | 1.122 | 1.06 |  | 24.608 |  |  | 0
| Well 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.233 | 0.161 | 0.277 | 0 | 0 | 0.234 | 0 | 0.002 | 0.237 | 0.182 | 0 | 0 | 0.37 | 0 | 0 | 0.307 | 0.288 | 0 | 0 | 0.625 | 0 |  | 2.916 |  |  | 0
| Total | 1.948 | 0.637 | 1.313 | 1.396 | 1.44 | 1.077 | 1.487 | 2.14 | 1.946 | 2.197 | 2.411 | 2.533 | 1.385 | 1.766 | 2.186 | 1.475 | 1.3938 | 2.398 | 1.905 | 1.866 | 1.711 | 2.865 | 2.147 | 1.615 | 2.716 | 2.881 | 2.482 | 2.156 | 3.175 | 2.41 |  | 59.0578 | 1.9686 | 3.175
Knollwood September
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 3 | 0 | 0 | 0 | 0 | 0.029 | 0 | 0.0234 | 0.0197 | 0.0197 | 0 | 0.038 | 0.0279 | 0 | 0.0113 | 0.0432 | 0 | 0 | 0.0153 | 0.0145 | 0.0204 | 0.0106 | 0.021 | 0.0226 | 0.0255 | 0.0282 | 0.022 | 0.0242 | 0.0449 | 0.0101 | 0.0152 |  | 0.4867 |  |  | 0
| Well 4 | 0.023 | 0 | 0 | 0 | 0 | 0.03 | 0.031 | 0.06 | 0.059 | 0.029 | 0.112 | 0.082 | 0 | 0 | 0.079 | 0 | 0.027 | 0.111 | 0.121 | 0 | 0 | 0.175 | 0.02 | 0.022 | 0.144 | 0.146 | 0.02 | 0 | 0.29 | 0 |  | 1.581 |  |  | 0
| Total | 0.023 | 0 | 0 | 0 | 0.029 | 0.03 | 0.0544 | 0.0797 | 0.0787 | 0.029 | 0.15 | 0.1099 | 0 | 0.0113 | 0.1222 | 0 | 0.027 | 0.1263 | 0.1355 | 0.0204 | 0.0106 | 0.196 | 0.0426 | 0.0475 | 0.1722 | 0.168 | 0.0442 | 0.0449 | 0.3001 | 0.0152 |  | 2.0677 | 0.068923 | 0.3001
Oct
October | Wekiva
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0 | 0.1368 | 0.1392 | 0 | 0.1705 | 0.0416 | 0 | 0 | 0 | 0 | 0 | 0.1074 | 0.0445 | 0 | 0 | 0.1208 | 0.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0934 | 0.1068 | 1.0262 |  |  | 0
| Well 6 | 0 | 0.1421 | 0.1485 | 0 | 0.184 | 0.0364 | 0 | 0 | 0 | 0 | 0 | 0.1065 | 0.0493 | 0 | 0 | 0.1261 | 0.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0941 | 0.1077 | 1.0613 |  |  | 0
| Well 7 | 0 | 0.21 | 0.218 | 0 | 0.253 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0.145 | 0.085 | 0 | 0 | 0.186 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.121 | 0.14 | 1.531 |  |  | 0
| Well 8 | 3.979 | 4.031 | 4.131 | 4.446 | 4.92 | 3.565 | 3.718 | 3.078 | 3.586 | 3.652 | 3.335 | 3.627 | 3.77 | 3.946 | 3.71 | 3.934 | 4.136 | 3.532 | 3.955 | 3.358 | 3.256 | 3.012 | 3.807 | 3.856 | 3.518 | 3.537 | 3.419 | 3.452 | 2.86 | 3.891 | 3.991 | 115.008 |  |  | 0
| Well 9 | 0 | 0.302 | 0.312 | 0 | 0.369 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0.166 | 0 | 0 | 0.267 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.827 |  |  | 0
| Total | 3.979 | 4.8219 | 4.9487 | 4.446 | 5.8965 | 3.818 | 3.718 | 3.078 | 3.586 | 3.652 | 3.335 | 4.1529 | 4.1148 | 3.946 | 3.71 | 4.6339 | 4.5098 | 3.532 | 3.955 | 3.358 | 3.256 | 3.012 | 3.807 | 3.856 | 3.518 | 3.537 | 3.419 | 3.452 | 2.86 | 4.1995 | 4.3455 | 120.4535 | 3.8856 | 5.8965
Des Pinar
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 |  |  | 0
| Well 1A | 0.978 | 1.152 | 1.282 | 1.309 | 1.068 | 1.532 | 0.813 | 0.719 | 0.878 | 0.936 | 0.762 | 0.87 | 1.174 | 0.93 | 0.891 | 0.967 | 0.975 | 0.783 | 0.81 | 0.79 | 0.736 | 0.76 | 0.764 | 0.868 | 0.698 | 0.772 | 0.848 | 0.707 | 0.615 | 0.933 | 0.877 | 28.197 |  |  | 0
| Well 2 | 0.768 | 0.901 | 1.013 | 1.029 | 0 | 2.04 | 0.633 | 0.56 | 0.692 | 0.732 | 0.594 | 0.69 | 1.023 | 0.831 | 0.812 | 0.895 | 0.903 | 0.722 | 0.748 | 0.736 | 0.682 | 0.703 | 0.668 | 0.824 | 0.664 | 0.745 | 0.831 | 0.703 | 0.61 | 0.935 | 0.913 | 24.6 |  |  | 0
| Well 2A | 0 | 0.301 | 0.272 | 0 | 0 | 0.563 | 0 | 0.003 | 0.086 | 0 | 0 | 0.145 | 0.264 | 0 | 0 | 0.32 | 0.261 | 0 | 0 | 0.17 | 0 | 0 | 0.241 | 0.196 | 0 | 0 | 0.27 | 0 | 0 | 0.284 | 0.266 | 3.642 |  |  | 0
| Total | 1.746 | 2.354 | 2.567 | 2.338 | 1.068 | 4.135 | 1.446 | 1.285 | 1.656 | 1.668 | 1.356 | 1.705 | 2.461 | 1.761 | 1.703 | 2.182 | 2.139 | 1.505 | 1.558 | 1.696 | 1.418 | 1.463 | 1.673 | 1.888 | 1.362 | 1.517 | 1.949 | 1.41 | 1.225 | 2.152 | 2.056 | 56.442 | 1.8207 | 4.135
Knollwood
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0 | 0.0245 | 0.0376 | 0 | 0.0223 | 0.0314 | 0.0328 | 0 | 0.0398 | 0 | 0 | 0 | 0.0207 | 0.0206 | 0.0003 | 0.0125 | 0.0155 | 0.0124 | 0.0222 | 0 | 0 | 0 | 0.0145 | 0.0113 | 0.0296 | 0 | 0.0219 | 0 | 0 | 0.0158 | 0.0094 | 0.3951 |  |  | 0
| Well 4 | 0.019 | 0.152 | 0.161 | 0 | 0 | 0.345 | 0 | 0.022 | 0 | 0 | 0 | 0.088 | 0.053 | 0.031 | 0.03 | 0.089 | 0.062 | 0.024 | 0 | 0 | 0.018 | 0.021 | 0.061 | 0.049 | 0 | 0 | 0.03 | 0 | 0.019 | 0 | 0.1 | 1.374 |  |  | 0
| Total | 0.019 | 0.1765 | 0.1986 | 0 | 0.0223 | 0.3764 | 0.0328 | 0.022 | 0.0398 | 0 | 0 | 0.088 | 0.0737 | 0.0516 | 0.0303 | 0.1015 | 0.0775 | 0.0364 | 0.0222 | 0 | 0.018 | 0.021 | 0.0755 | 0.0603 | 0.0296 | 0 | 0.0519 | 0 | 0.019 | 0.0158 | 0.1094 | 1.7691 | 0.057068 | 0.3764
Nov
nov | Wekiva November
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 5 | 0 | 0 | 0 | 0 | 0 | 0.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.1221 |  |  | 0
| Well 6 | 0 | 0 | 0 | 0 | 0 | 0.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.1233 |  |  | 0
| Well 7 | 0 | 0 | 0 | 0 | 0 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.184 |  |  | 0
| Well 8 | 3.581 | 4.054 | 4.454 | 3.734 | 3.438 | 3.661 | 4.526 | 3.223 | 3.767 | 3.778 | 3.574 | 3.484 | 3.972 | 4.239 | 3.313 | 3.819 | 3.832 | 3.726 | 3.303 | 4.074 | 4.493 | 3.562 | 3.772 | 3.998 | 4.362 | 3.272 | 4.183 | 4.371 | 3.243 | 4.631 |  | 115.439 |  |  | 0
| Well 9 | 0 | 0 | 0 | 0 | 0 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.267 |  |  | 0
| Total | 3.581 | 4.054 | 4.454 | 3.734 | 3.438 | 3.9823 | 4.526 | 3.223 | 3.767 | 3.778 | 3.574 | 3.484 | 3.972 | 4.239 | 3.313 | 3.819 | 3.832 | 3.726 | 3.303 | 4.074 | 4.493 | 3.562 | 4.1471 | 3.998 | 4.362 | 3.272 | 4.183 | 4.371 | 3.243 | 4.631 |  | 116.1354 | 3.8712 | 4.631
Des Pinar November
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.002 |  |  | 0
| Well 1A | 0.877 | 0.624 | 1.233 | 1.039 | 0.683 | 0.787 | 0.88 | 0.851 | 0.719 | 0.819 | 0.786 | 0.63 | 0.778 | 0.954 | 0.559 | 0.769 | 0.851 | 0.634 | 0.726 | 0.805 | 0.832 | 0.826 | 0.684 | 1.147 | 0.682 | 0.682 | 0.741 | 0.702 | 0.907 | 0.685 |  | 23.892 |  |  | 0
| Well 2 | 0.895 | 0.839 | 1.068 | 1.073 | 0.714 | 0.837 | 0.943 | 0.899 | 0.766 | 0.876 | 0.847 | 0.681 | 0.852 | 1.04 | 0.609 | 0.845 | 0.934 | 0.695 | 0.812 | 0.957 | 1 | 0.993 | 0.826 | 1.377 | 0.816 | 0.816 | 0.896 | 0.853 | 1.092 | 0.828 |  | 26.679 |  |  | 0
| Well 2A | 0 | 0.462 | 0.145 | 0 | 0 | 0.309 | 0.212 | 0 | 0.168 | 0.145 | 0 | 0 | 0.266 | 0.222 | 0 | 0 | 0.323 | 0 | 0 | 0.294 | 0.25 | 0 | 0.181 | 0.465 | 0 | 0 | 0.28 | 0.225 | 0 | 0.312 |  | 4.259 |  |  | 0
| Total | 1.772 | 1.925 | 2.446 | 2.112 | 1.397 | 1.933 | 2.037 | 1.75 | 1.653 | 1.84 | 1.633 | 1.311 | 1.896 | 2.216 | 1.168 | 1.614 | 2.108 | 1.329 | 1.538 | 2.056 | 2.082 | 1.819 | 1.691 | 2.989 | 1.498 | 1.498 | 1.917 | 1.78 | 1.999 | 1.825 |  | 54.832 | 1.8277 | 2.989
Knollwood November
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | Total | Avg | Max | Proof
| Well 3 | 0 | 0.0347 | 0.0301 | 0 | 0 | 0.0321 | 0.0192 | 0 | 0 | 0.0282 | 0 | 0 | 0.0267 | 0.0003 | 0 | 0.0332 | 0 | 0 | 0.0014 | 0.0206 | 0.015 | 0 | 0.0052 | 0.0262 | 0 | 0 | 0.0132 | 0.0132 | 0.0093 | 0.0126 |  | 0.3212 |  |  | 0
| Well 4 | 0 | 0.053 | 0.033 | 0 | 0 | 0.031 | 0.041 | 0.007 | 0.022 | 0 | 0 | 0 | 0.065 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0.03 | 0.025 | 0 | 0.046 | 0.033 | 0 | 0 | 0.046 | 0.027 | 0 | 0.042 |  | 0.531 |  |  | 0
| Total | 0 | 0.0877 | 0.0631 | 0 | 0 | 0.0631 | 0.0602 | 0.007 | 0.022 | 0.0282 | 0 | 0 | 0.0917 | 0.0003 | 0 | 0.0332 | 0.03 | 0 | 0.0014 | 0.0506 | 0.04 | 0 | 0.0512 | 0.0592 | 0 | 0 | 0.0592 | 0.0402 | 0.0093 | 0.0546 |  | 0.8522 | 0.028407 | 0.0917
Dec
December | Wekiva
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 5 | 0.0644 | 0.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1875 |  |  | 0
| Well 6 | 0.065 | 0.1251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1901 |  |  | 0
| Well 7 | 0.145 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.281 |  |  | 0
| Well 8 | 3.717 | 2.973 | 3.318 | 4.143 | 4.001 | 3.585 | 4.284 | 4.181 | 3.989 | 3.294 | 4.123 | 3.897 | 3.173 | 3.514 | 3.753 | 3.026 | 3.232 | 3.3 | 3.303 | 3.055 | 3.761 | 3.477 | 2.978 | 3.154 | 3.141 | 3.551 | 3.159 | 3.122 | 3.159 | 3.101 | 2.865 | 107.329 |  |  | 0
| Well 9 | 0.141 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 3.731 |  |  | 0
| Total | 4.1324 | 3.6472 | 3.318 | 4.143 | 4.001 | 3.585 | 4.284 | 4.181 | 3.989 | 3.294 | 4.123 | 3.897 | 3.173 | 3.514 | 3.753 | 3.026 | 3.232 | 3.3 | 3.303 | 3.055 | 3.761 | 3.477 | 2.978 | 3.154 | 6.441 | 3.551 | 3.159 | 3.122 | 3.159 | 3.101 | 2.865 | 111.7186 | 3.6038 | 6.441
Des Pinar
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 1 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 |  |  | 0
| Well 1A | 1.038 | 0.625 | 0.617 | 0.762 | 0.758 | 0.7 | 0.751 | 0.745 | 1.042 | 0.626 | 0.812 | 0.764 | 0.428 | 0.688 | 0.682 | 0.66 | 0.534 | 0.567 | 0.691 | 0.493 | 0.742 | 0.762 | 0.407 | 0.389 | 0.627 | 0.707 | 0.421 | 0.639 | 0.618 | 0.459 | 0.435 | 20.189 |  |  | 0
| Well 2 | 1.251 | 0.746 | 0.745 | 0.918 | 0.915 | 0.842 | 0.905 | 0.901 | 1.254 | 0.751 | 0.982 | 0.922 | 0.513 | 0.78 | 0.822 | 0.79 | 0.634 | 0.689 | 0.83 | 0.589 | 0.893 | 0.996 | 0.475 | 0.466 | 0.748 | 0.798 | 0.493 | 0.776 | 0.739 | 0.544 | 0.518 | 24.225 |  |  | 0
| Well 2A | 0.472 | 0.002 | 0 | 0.243 | 0.37 | 0 | 0.238 | 0.238 | 0.157 | 0 | 0.364 | 0.19 | 0 | 0.094 | 0.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.668 |  |  | 0
| Total | 2.761 | 1.375 | 1.362 | 1.923 | 2.043 | 1.542 | 1.894 | 1.884 | 2.453 | 1.377 | 2.158 | 1.876 | 0.941 | 1.562 | 1.628 | 1.45 | 1.168 | 1.256 | 1.521 | 1.082 | 1.635 | 1.934 | 0.882 | 0.855 | 1.375 | 1.505 | 0.914 | 1.415 | 1.357 | 1.003 | 0.953 | 47.084 | 1.5188 | 2.761
Knollwood
| Wells | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | Proof
| Well 3 | 0.0125 | 0 | 0.0003 | 0.0115 | 0.0386 | 0 | 0.0128 | 0.0121 | 0 | 0 | 0.0124 | 0 | 0 | 0.0252 | 0 | 0 | 0 | 0.0389 | 0 | 0 | 0.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.179 |  |  | 0
| Well 4 | 0.054 | 0 | 0.024 | 0.025 | 0.029 | 0 | 0.051 | 0.048 | 0 | 0 | 0.054 | 0.03 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0.001 | 0.01 | 0 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 |  |  | 0
| Total | 0.0665 | 0 | 0.0243 | 0.0365 | 0.0676 | 0 | 0.0638 | 0.0601 | 0 | 0 | 0.0664 | 0.03 | 0 | 0.0252 | 0.04 | 0 | 0 | 0.0389 | 0.001 | 0.01 | 0.0147 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.614 | 0.019806 | 0.069
Note on B20: Wells 3 & 4 feed the hydro tank