## Table Staff-36 Updated Analysis
Florida Power & Light Company
Docket No. 150196-EI
Staff's Second Set of Interrogatories
Interrogatory No. 36 - Supplemental
Attachment No. 1
Tab 1 of 1
Table Staff Supplemental-36
Updated Analysis
Plant Specifications for Generation Options - Staff Supplemental Interrogatory 36
[17 empty] | Emission Rates |  |  |  | Linear Facilities
Site | Manufacturer | Model of CT | Generating Technology1 | Capacity Summer Peak (95oF) MW | Capacity Winter Peak (35oF) MW | Planned Outage Factor (%) | Forced Outage Factor (%) | Equivalent Availability Factor (%) | Resulting Capacity Factor (Approx. %) | Overnight Capital Costs (2019$ / Summer KW) |  | Heat Rate (Base @ 75oF, 100%) BTU/kWh | Annual Fixed O&M3 (2019$ Millions) | Annual Variable O&M4 ($/MWh) | Primary Fuel | Backup Fuel | NOx Emission Rates (lb/mmbtu) | CO Emission Rates (lb/mmbtu) | SO2 Emission Rates (lb/mmbtu) | Primary Water Source | Gas | Transmission
Okeechobee | GE | 7HA.02 | 3x3x1 | 1633 | 1606 | 3.5 | 1 | 95.5 | 80 | 678.6522 | 2 | 6249 | 27.3983 | 0.2612 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | GE | 7HA.02 | 3x3x1 | 1622 | 1595 | 3.5 | 1 | 95.5 | 80 | 667.961 |  | 6304 | 27.3983 | 0.26297 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | GE | 7FA.05 | 6x0x0 | 1386 | 1337 | 3 | 1 | 96 | 5 | 484.8958 |  | 10074 | 4.5302 | 0.0088121 | Natural Gas | Light Fuel Oil | 0.03 | 0.015 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | GE | 7FA.05 | 7x0x0 | 1617 | 1560 | 3 | 1 | 96 | 5 | 477.9458 |  | 10074 | 4.9324 | 0.0088121 | Natural Gas | Light Fuel Oil | 0.03 | 0.015 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | GE | 7FA.05 | 5x0x0 | 1155 | 1114.2857 | 3 | 1 | 96 | 5 | 485 |  | 10074 | 3.7752 | 0.0088121 | Natural Gas | Light Fuel Oil | 0.03 | 0.015 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | Mitsubishi | J | 3x3x1 | 1418 | 1562.228 | 3.5 | 1 | 95.5 | 80 | 730.3786 |  | 6332.1714 | 55.9546 | 0.26519 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Okeechobee | Siemens | H | 3x3x1 | 1322 | 1427 | 3.5 | 1 | 95.5 | 80 | 749.4889 |  | 6515.1755 | 41.3539 | 0.26519 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 5
Notes:
1 Generating technology provided describes the number of advanced combustion turbines followed by the number of heat recovery
steam generators followed by the number of steam turbines (e.g., Row 1 is an Okeechobee generating technology with three (3)
advanced combustion turbines, three (3) heat recovery steam generators, and a single (1) steam turbine)
2 The total installed cost in 2019$ for the 1,633 MW Okeechobee CC unit is $1,231.67 million. This total consists of $1,056.24 million
for the power block, $52.00 million for the transmission interconnection and integration, and $123.43 million for AFUDC.
3 Annual fixed O&M value includes capital replacement costs and fixed O&M presented as a levelized value in 2019 $
4 Variable O&M represents the value for 2019
5 No new linear transmission facilities