## Crownwood
252/090 (635) - Crownwood 2019
| Operating Permit: | FLA012680 |  |  |  | Expires: | 2023-04-23
| Plant Permitted Capacity: | 0.040 mgd TMADF | [6 empty] | From Historical Data | [8 empty] | Hyperlinks!A1
| Perc Ponds/Surf Discharge: | 0.040 mgd | [6 empty] | From Daily Flow Worksheet
Manual data entry from DMR
Hyperlinks!A1 | [12 empty] | Note: The 'Word' file on UIWaterMain. Copy/Paste Special/Transpose daily flows from this doc.
| Flow (FLW-01) | Flow (FLW-01) | Flow (FLW-01) | Flow (FLW-01) | CBOD5 |  |  | TSS |  |  | pH |  | Fecal Coliform |  |  | TRC | Total Nitrogen
| Mo Flow | 3MRA | Mo Avg | Peak | An Avg | Mo Avg | Max | An Avg | Mo Avg | Max | Min | Max | An Avg | MoGeoMean | Max | Min
| mgd | mgd | mgd | mgd | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | S.U. | S.U | #/100ml | #/100ml | #/100ml | mg/L | mg/L
Limit | Total | 0.040 (AADF) | Report |  | 20 | 30 | 60 | 20 | 30 | 60 | 6 | 8.5 | 200 | 200 | 800 | 0.5 | Qtrly Max
2019-01-01 | 0.875 | 0.025 | 0.028 | 0.039 | 2 | <2.0 | <2.0 | 2 | 2 | 2 | 7.3 | 7.5 | 4 | <1.0 | <1.0 | 1.1 | MNR
February | 0.675 | 0.026 | 0.024 | 0.036 | 2 | 3.1 | 3.1 | 6 | 6 | 6 | 7.3 | 7.6 | 4 | <2.0 | <2.0 | 1.1 | 14.4
March | 0.71 | 0.025 | 0.023 | 0.035 | 2.2 | 2.5 | 2.5 | 3 | 11 | 11 | 7.5 | 7.8 | 2.7 | <2.0 | <2.0 | >2.2 | MNR
April | 0.785 | 0.024 | 0.026 | 0.037 | 2.2 | <2.0 | <2.0 | 3.4 | 5 | 5 | 7.4 | 7.6 | 2.8 | <1.0 | <1.0 | 2 | MNR
May | 0.696 | 0.024 | 0.022 | 0.038 | 2.3 | 3.8 | 3.8 | 4 | 10 | 10 | 7.5 | 7.6 | 2.2 | <1.0 | <1.0 | 1 | 52
June | 0.42 | 0.021 | 0.015 | 0.026 | 2.4 | 2 | 2 | 4.1 | 3 | 3 | 7.4 | 7.6 | 2.3 | <2.0 | <2.0 | >2.2 | MNR
July | 0.588 | 0.019 | 0.019 | 0.036 | 2.3 | <2.0 | <2.0 | 4.1 | 2 | 2 | 7.4 | 7.6 | 1.8 | <2.0 | <2.0 | >2.2 | MNR
August | 0.762 | 0.025 | 0.025 | 0.052 | 1.8 | <2.0 | <2.0 | 4.1 | <1 | <1 | 7.3 | 7.6 | 1.8 | <1.0 | <1.0 | >2.2 | 1.3
September | 0.528 | 0.021 | 0.018 | 0.026 | 2 | <2.0 | <2.0 | 4 | 2 | 2 | 7.3 | 7.6 | 2 | 1 | 1 | >2.2 | MNR
October | 0.224 | 0.02 | 0.017 | 0 | 1.8 | <2.0 | <2.0 | 4 | <1.0 | <1.0 | 7.4 | 7.6 | 1.8 | <1.0 | <1.0 | >2.2 | MNR
November | 0.494 | 0.017 | 0.016 | 0.022 | 1.69 | <2.0 | <2.0 | 3.8 | <1.0 | <1.0 | 7.4 | 7.6 | 1.5 | <1.0 | <1.0 | >2.2 | MNR
December | 0.564 | 0.017 | 0.018 | 0.027 | 1.6 | <2.0 | <2.0 | 4.1 | 8 | 8 | 7.4 | 7.8 | 0.7 | 11 | 11 | >2.2 | MNR
YTD Flow | 7.321
Average | 0.61008 | 0.022 | 0.020917 | 0.031167 | 2.0242 |  |  | 3.8833 | 5.4444 | 5.4444 |  |  | 2.3
Minimum | 0.224 | 0.017 | 0.015 | 0 | 1.6 | 2 | 2 | 2 | 2 | 2 | 7.3 | 7.5 | 0.7 | 1 | 1 | 1 | 1.3
Maximum | 0.875 | 0.026 | 0.028 | 0.052 | 2.4 | 3.8 | 3.8 | 6 | 11 | 11 | 7.5 | 7.8 | 4 | 11 | 11 | 2 | 52
Historical Data
| REUSE MOAVG | CBOD MOAVG | Reuse 3MRA
R12MOAVG |  |  |  | Change formula before entering the next month's data
2018-01-01 | 0.021 | <2.0 | 0.021 | Jacquee
February | 0.025 | 4.1 | 0.023 | 1 | Copy/Paste Value' the 2018 Historical Data from the 2018 DMR Summaries workbook.
March | 0.023 | 3.2 | 0.023 | 2 | Enter in the formulas/links into the 2019 Table below and also the formulas in row 36
April | 0.025 | 2.1 | 0.024333
May | 0.021 | 2.2 | 0.023
June | 0.02 | <2.0 | 0.022
July | 0.02 | 2.2 | 0.020333
August | 0.019 | 7 | 0.019667
September | 0.02 | <2.0 | 0.019667
October | 0.017 | <2.0 | 0.018667
November | 0.021 | 2.8 | 0.019333
December | 0.027 | <2.0 | 0.021667
2019-01-01 | 0.028 | <2.0 | 0.025333
February | 0.024 | 3.1 | 0.026333
March | 0.023 | 2.5 | 0.025
April | 0.026 | <2.0 | 0.024333
May | 0.022 | 3.8 | 0.023667
June | 0.015 | 2 | 0.021
July | 0.019 | <2.0 | 0.018667
August | 0.025 | <2.0 | 0.019667
September | 0.018 | <2.0 | 0.020667
October | 0.017 | <2.0 | 0.02
November | 0.016 | <2.0 | 0.017
December | 0.018 | <2.0 | 0.017
Note on C8: From page 1 of DMR 'Flow, To R-001 PARMCode 50050 FLW-01' (AADF)
Note on D8: From page 1 of DMR Flow, To R-001 PARM Code 50050 (Mo.Avg.)'
Note on F8: From page 1 of DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082'
Note on I8: From page 1 of DMR 'Solids, Total Suspended PARM Code 00530 EFA-01'
Note on L8: From page 2 of DMR pH PARM Code 00406 EFA-01'
Note on N8: From page 2 of DMR 'Coliform, Fecal PARM Code 74055 EFA-01'
Note on Q8: From page 2 of DMR Total Chlorine Residual (For Disinfection) PARM Code 50060 EFA-01'
Note on R8: From page 2 of DMR Nitrogen, Nitrate, Total (as N) PARM Code 00620 EFA-01'

## Crownwood Flow Summary
2019 Crownwood - DMR Flow Summary | [5 empty] | Hyperlinks!A1
FLW-01 | Note: See Word.doc file to copy the FLW-1 daily flows from. Copy/past to B21 then format the cells to number with 3 decimal places. Then copy/paste value/tranpose to the applicable month Row.
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg | Max
2019-01-01 | 0.039 | 0.026 | 0.029 | 0.029 | 0.024 | 0.026 | 0.024 | 0.026 | 0.026 | 0.028 | 0.036 | 0.024 | 0.027 | 0.026 | 0.016 | 0.019 | 0.024 | 0.02 | 0.025 | 0.024 | 0.037 | 0.032 | 0.03 | 0.032 | 0.038 | 0.03 | 0.031 | 0.033 | 0.038 | 0.027 | 0.029 |  | 0.875 | 0.028226 | 0.039 | 03/08/17 email to Marlin. Flow toal on Part B is incorrect.
February | 0.036 | 0.029 | 0.028 | 0.027 | 0.016 | 0.025 | 0.023 | 0.03 | 0.026 | 0.03 | 0.029 | 0.026 | 0.021 | 0.025 | 0.021 | 0.023 | 0.021 | 0.026 | 0.022 | 0.013 | 0.029 | 0.023 | 0.022 | 0.023 | 0.024 | 0.022 | 0.022 | 0.013 |  |  |  |  | 0.675 | 0.024107 | 0.036
March | 0.011 | 0.033 | 0.033 | 0.024 | 0.012 | 0.022 | 0.021 | 0.024 | 0.025 | 0.024 | 0.029 | 0.02 | 0.019 | 0.023 | 0.022 | 0.02 | 0.019 | 0.028 | 0.012 | 0.03 | 0.024 | 0.035 | 0.02 | 0.022 | 0.022 | 0.03 | 0.018 | 0.022 | 0.027 | 0.012 | 0.027 |  | 0.71 | 0.022903 | 0.035
April | 0.028 | 0.021 | 0.02 | 0.03 | 0.023 | 0.023 | 0.023 | 0.026 | 0.019 | 0.023 | 0.017 | 0.025 | 0.02 | 0.02 | 0.022 | 0.01 | 0.029 | 0.035 | 0.037 | 0.037 | 0.037 | 0.037 | 0.027 | 0.021 | 0.031 | 0.029 | 0.021 | 0.037 | 0.036 | 0.021 |  |  | 0.785 | 0.026167 | 0.037
May | 0.034 | 0.028 | 0.038 | 0.028 | 0.03 | 0.028 | 0.014 | 0.027 | 0.028 | 0.036 | 0.029 | 0.029 | 0.032 | 0.035 | 0.025 | 0.014 | 0.016 | 0.016 | 0.015 | 0.016 | 0.01 | 0.021 | 0.017 | 0.021 | 0.016 | 0.015 | 0.018 | 0.015 | 0.014 | 0.01 | 0.021 |  | 0.696 | 0.022452 | 0.038
June | 0.016 | 0.015 | 0.01 | 0.015 | 0.026 | 0.008 | 0.016 | 0.018 | 0.018 | 0.024 | 0.014 | 0.016 | 0.013 | 0.008 | 0.01 | 0.01 | 0.008 | 0..019 | 0.015 | 0.01 | 0.025 | 0.023 | 0.015 | 0.013 | 0.009 | 0.023 | 0.011 | 0.02 | 0.006 | 0.005 |  |  | 0.42 | 0.014483 | 0.026
July | 0.005 | 0.015 | 0.019 | 0.019 | 0.014 | 0.018 | 0.015 | 0.014 | 0.015 | 0.018 | 0.01 | 0.024 | 0.018 | 0.018 | 0.018 | 0.013 | 0.017 | 0.019 | 0.018 | 0.018 | 0.018 | 0.01 | 0.023 | 0.018 | 0.027 | 0.036 | 0.032 | 0.03 | 0.03 | 0.018 | 0.021 |  | 0.588 | 0.018968 | 0.036
August | 0.019 | 0.024 | 0.016 | 0.018 | 0.018 | 0.009 | 0.02 | 0.019 | 0.023 | 0.016 | 0.017 | 0.014 | 0.013 | 0.019 | 0.022 | 0.016 | 0.051 | 0.052 | 0.044 | 0.035 | 0.03 | 0.036 | 0.036 | 0.034 | 0.034 | 0.025 | 0.024 | 0.02 | 0.022 | 0.019 | 0.017 |  | 0.762 | 0.024581 | 0.052
September | 0.026 | 0.025 | 0.014 | 0.025 | 0.019 | 0.026 | 0.018 | 0.019 | 0.018 | 0.01 | 0.017 | 0.022 | 0.016 | 0.018 | 0.017 | 0.015 | 0.017 | 0.017 | 0.01 | 0.024 | 0.017 | 0.016 | 0.016 | 0.014 | 0.011 | 0.014 | 0.017 | 0.016 | 0.016 | 0.018 |  |  | 0.528 | 0.0176 | 0.026
October | 0.016 | 0.01 | 0.02 | 0.023 | 0 | 0 | 0.018 | 0 | 0 | 0.018 | 0 | 0 | 0.017 | 0 | 0 | 0.013 | 0 | 0 | 0.02 | 0 | 0 | 0.016 | 0 | 0 | 0.024 | 0 | 0 | 0.013 | 0 | 0 | 0.016 | 0 | 0.224 | 0.017 | 0
November | 0.018 | 0.009 | 0.009 | 0.018 | 0.01 | 0.016 | 0.016 | 0.019 | 0.018 | 0.018 | 0.018 | 0.014 | 0.01 | 0.014 | 0.022 | 0.02 | 0.019 | 0.019 | 0.018 | 0.017 | 0.015 | 0.016 | 0.022 | 0.019 | 0.019 | 0.012 | 0.02 | 0.021 | 0.018 | 0.01 |  |  | 0.494 | 0.016467 | 0.022
December | 0.018 | 0.018 | 0.027 | 0.014 | 0.012 | 0.02 | 0.023 | 0.017 | 0.016 | 0.016 | 0.011 | 0.019 | 0.01 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018 | 0.004 | 0.019 | 0.026 | 0.024 | 0.016 | 0.019 | 0.022 | 0.02 | 0.019 | 0.022 | 0.023 | 0.019 |  | 0.564 | 0.018194 | 0.027
FLW-01
1 | 0.018
2 | 0.018
3 | 0.027
4 | 0.014
5 | 0.012
6 | 0.02
7 | 0.023
8 | 0.017
9 | 0.016
10 | 0.016
11 | 0.011
12 | 0.019
13 | 0.01
14 | 0.019
15 | 0.019
16 | 0.018
17 | 0.018
18 | 0.018
19 | 0.018
20 | 0.004
21 | 0.019
22 | 0.026
23 | 0.024
24 | 0.016
25 | 0.019
26 | 0.022
27 | 0.02
28 | 0.019
29 | 0.022
30 | 0.023
31 | 0.019