## Mid County
250/261 (645) - Mid County 2019
| Operating Permit No.: | FL0034789-008-DW1 |  |  |  | Expires: | 2021-08-04
| Plant Permitted Capacity: | 0.900 mgd AADF | [9 empty] | From Historical Data
| Surface Discharge: | 0.900 mgd | [9 empty] | From Daily Flow Worksheet
| Reuse/Public Access: | N/A | [9 empty] | Manual data entry from DMR
Hyperlinks!A1
FLW-01
| CBOD5 | CBOD5 |  | TSS | TSS |  | pH |  | Fecal Coliform |  | TRC |  | Nitrogen | Nitrogen |  | Phosphor- ous | Phosphorous |  | D.O. | Total Flow | Total Flow |  | CBOD | TSS
| R12MA | Mo Avg | Max | AnAvg | MoAvg | Max | Min | Max | Min | Max | Chl (Min) | Dechl (Max) | R12MA | MoAvg | Max | R12MA | MoAvg | Max | Min | R12MA | Mo Avg | Peak | mg/L | mg/L
Limit | 5 | 6.25 | 10 | 5 | 6.25 | 10 | 6 | 8.5 | 75% ND | 25 | 1 | 0.01 | 3 | 3.75 | 6 | 1 | 1.25 | 2 | 5 | Report | Report | Flow | INF-01 | INF-01
2019-01-01 | 3.7617 | 4.72 | 9.7 | 0.96364 | 0.36 | 1.8 | 6 | 8.05 | 100% | <1 | 1.5 | <0.01 | 1.63 | 1.77 | 2.7 | 0.37917 | 0.6 | 0.84 | 6.7 | 0.37917 | 0.75626 | 0.897 | 200 | 200
February | 3.5867 | 2.78 | 4.5 | 0.88636 | 0.75 | 3 | 6.7 | 7.77 | 100% | <1 | 1.5 | <0.01 | 1.6233 | 0.83 | 2 | 0.37333 | 0.34 | 0.92 | 6.1 | 0.37333 | 0.85807 | 1.255 | 180 | 150
March | 2.9658 | 1.08 | 4.3 | 0.82909 | 0.57 | 1.6 | 6.24 | 7.92 | 100% | <1 | 1 | 0.01 | 1.6242 | 0.93 | 2 | 0.33917 | 0.1 | 0.17 | 6.5 | 0.33917 | 0.87416 | 1.176 | 92 | 180
April | 2.96 | 1.68 | 4.9 | 0.80182 | 0.2 | 1 | 6 | 7.66 | 100% | <1 | 1 | 0.01 | 1.5308 | 0.86 | 1.4 | 0.33917 | 0.33 | 0.27 | 6.8 | 0.33917 | 0.78763 | 0.909 | 140 | 190
May | 2.7083 | 1.8 | 5.5 | 0.68545 | 0.2 | 1 | 6.02 | 7.86 | 100% | <1 | 1.1 | 0.01 | 1.3225 | 0.98 | 1.2 | 0.355 | 0.29 | 0.71 | 7 | 0.355 | 0.76484 | 0.89 | 150 | 230
June | 2.4808 | 0.5 | 2 | 0.61727 | 0.25 | 1 | 6.1 | 7.84 | 100% | <1 | 1.1 | 0.01 | 1.2375 | 0.54 | 0.94 | 0.31417 | 0.13 | 0.31 | 6.9 | 0.31417 | 1.042 | 1.936 | 150 | 260
July | 2.3864 | <2 | <2 | 0.611 | <1 | <1 | 6.34 | 7.83 | 100% | <1 | 1.2 | 0.01 | 1.1458 | 0.68 | 1.1 | 0.32583 | 0.48 | 1 | 6.9 | 0.32583 | 1.2622 | 1.861 | 210 | 250
August | 2.542 | <2 | <2 | 0.611 | <1 | <1 | 6.1 | 7.5 | 100% | <1 | 1.4 | 0.01 | 1.0167 | 0.31 | 0.52 | 0.32658 | 0.069 | 0.14 | 7 | 0.32658 | 1.2063 | 1.944 | 140 | 120
September | 2.544 | 1 | 1 | 0.636 | 0.5 | 0.5 | 6 | 8.4 | 100% | <1 | 1.3 | 0.01 | 0.92167 | 0.34 | 0.38 | 0.32067 | 0.049 | 0.05 | 6.3 | 0.32067 | 0.89983 | 1.151 | 110 | 220
October | 2.5622 | <2 | <2 | 0.44222 | <1 | <1 | 6.4 | 8 | 100% | <1 | 1 | 0.01 | 0.87667 | 0.9 | 3.6 | 0.26567 | 0.05 | 0.05 | 6.7 | 0.26567 | 0.85923 | 1.38 | 170 | 130
November | 1.97 | <2 | <2 | 0.46625 | <1 | 0.5 | 6 | 8.2 | 100% | <1 | 1.1 | 0.01 | 0.755 | 0.2 | 0.27 | 0.2165 | 0.05 | 0.05 | 7.48 | 0.2165 | 0.73437 | 0.957 | 250 | 230
December | 1.9371 | <2 | <2 | 0.40429 | <1 | <1 | 6.9 | 7.7 | 100% | <1 | 1 | 0.01 | 0.71667 | 0.26 | 0.27 | 0.2115 | 0.05 | 0.05 | 6.7 | 0.2115 | 0.77003 | 1.213 | 300 | 230
Average | 2.7004 | 1.9371 | 4.5571 | 0.66287 | 0.40429 | 1.3 | 6.2333 | 7.8942 |  |  |  |  | 1.2001 | 0.71667 |  | 0.3139 | 0.2115 | 0.38 | 6.7567 | 0.3139 | 0.90124 | 1.2974 | 174.3333 | 199.1667
Minimum | [6 empty] | 6 |  | 1 |  | 1 | [7 empty] | 6.1 |  |  |  | 92 | 120
Maximum | 3.7617 | 4.72 | 9.7 | 0.96364 | 0.75 | 3 |  | 8.4 | 1 | 0 |  | 0.01 | 1.63 | 1.77 | 3.6 | 0.37917 | 0.6 | 1 | 7.48 | 0.37917 | 1.2622 | 1.944 | 300 | 260
Historical Data
Flow
| MoAvg | 12 Mo Avg | 3MoAvg | CBOD | TSS | TN | N12Mo | TP | P12Mo
January, 2018 | 0.68826 | 0.76158 | 0.75845 | 6.34 | 1.16 | 1.79 | 1.411 | 0.28 | 0.38
February | 0.7935 | 0.77155 | 0.75844 | 4.88 | 1.6 | 0.91 | 1.391 | 0.41 | 0.387
March | 0.69181 | 0.77393 | 0.72452 | 8.53 | 1.2 | 0.92 | 1.312 | 0.51 | 0.393
April | 0.71837 | 0.77769 | 0.73456 | 1.75 | 0.5 | 1.98 | 1.43 | 0.33 | 0.37
May | 0.74039 | 0.78282 | 0.71685 | 4.82 | 1.48 | 3.48 | 1.692 | 0.1 | 0.337
June | 0.74697 | 0.7814 | 0.73524 | 3.23 | 1 | 1.56 | 1.758 | 0.62 | 0.341
July | 0.77694 | 0.77874 | 0.75476 | 3.52 | 0.68 | 1.78 | 1.797 | 0.34 | 0.341
August | 0.99497 | 0.79159 | 0.83962 | 0.83 | <1 | 1.86 | 1.831 | 0.06 | 0.323
September | 1.0438 | 0.79797 | 0.93858 | 0.98 | 0.25 | 1.48 | 1.871 | 0.12 | 0.308
October | 0.79394 | 0.798 | 0.94425 | 2.38 | 2.38 | 1.44 | 1.72 | 0.71 | 0.348
November | 0.694 | 0.78971 | 0.84392 | 7.3 | 0.25 | 1.66 | 1.7145 | 0.64 | 0.37455
December | 0.852 | 0.79458 | 0.77998 | 2.2 | 0.9 | 0.72 | 1.6317 | 0.11 | 0.3525
January, 2019 | 0.75626 | 0.80025 | 0.76742 | 4.72 | 0.36 | 1.77 | 1.63 | 0.6 | 0.37917 |  | Jacquee
February | 0.85807 | 0.80563 | 0.82211 | 2.78 | 0.75 | 0.83 | 1.6233 | 0.34 | 0.37333 |  | 1 | Copy/Paste Value' the 2018 Historical Data from the 2018 DMR Summaries workbook.
March | 0.87416 | 0.82082 | 0.8295 | 1.08 | 0.57 | 0.93 | 1.6242 | 0.1 | 0.33917 |  |  | Enter in the formulas/links into the 2019 Table below and also the formulas in row 36
April | 0.78763 | 0.8266 | 0.83996 | 1.68 | 0.2 | 0.86 | 1.5308 | 0.33 | 0.33917
May | 0.76484 | 0.82863 | 0.80888 | 1.8 | 0.2 | 0.98 | 1.3225 | 0.29 | 0.355
June | 1.042 | 0.85322 | 0.86482 | 0.5 | 0.25 | 0.54 | 1.2375 | 0.13 | 0.31417
July | 1.2622 | 0.89366 | 1.023 | <2 | <1 | 0.68 | 1.1458 | 0.48 | 0.32583
August | 1.2063 | 0.91127 | 1.1702 | <2 | <1 | 0.31 | 1.0167 | 0.069 | 0.32658
September | 0.89983 | 0.89927 | 1.1228 | 1 | 0.5 | 0.34 | 0.92167 | 0.049 | 0.32067
October | 0.85923 | 0.90471 | 0.98845 | <2 | <1 | 0.9 | 0.87667 | 0.05 | 0.26567
November | 0.73437 | 0.90808 | 0.83114 | <2 | <1 | 0.2 | 0.755 | 0.05 | 0.2165
December | 0.77003 | 0.90124 | 0.78787 | <2 | <1 | 0.26 | 0.71667 | 0.05 | 0.2115
Note on C10: From page 1 of DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082 EFD-01
Note on H10: From page 2 of DMR 'pH PARM Code 00400 EFD-01'
Note on L10: From page 2 of the DMR 'Total Residual Chlorine (For disinfection) PARM Code 50060 EFA-01'
Note on O10: From page 2 of DMR 'Nitrogen, Total PARM Code 00600 EFD-01'
Note on R10: From page 2 of DMR 'Phosphorus, Total (as P) PARMCode 00665 EFD-01'
Note on T10: From page 2 of DMR Oxygen, Dissolved (DO) PARM Code 00300 EFD-01
Note on F11: From page 1 of DMR 'Solids, Total Suspended PARM Code 00530 EFD-01'
Note on G11: From page 2 of DMR 'Solids, Total Suspended PARM Code 00530 EFB-01'
Note on J11: From page 2 of DMR 'Coliform, Fecal % less than detection PARM Code 51005 EFD-01'
Note on K11: From page 2 of DMR Coliform, Fecal PARM Code 74055 EFD-01'
Note on L11: From page 2 of the DMR 'Total Residual Chlorine (For disinfection) PARM Code 50060 EFA-01'
Note on M11: From page 2 of DMR 'Total Residual Chlorine (for Dechlorination) PARM Code 50060 EFD-01'
Note on C19: Jacquee Chandler: Lee said this is fine
Note on D19: Jacquee Chandler: Lee said this is fine.

## Mid County Flow Summary
2019 Mid County DMR Flow Summary
Hyperlinks!A1
Note: David Worell to provide plant flow summary every month. (WWTP Log workbook - Excel) Copy, paste special,-value-transpose to this worksheet.
FLW-01
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max | RF
2019-01-01 | 0.818 | 0.847 | 0.865 | 0.876 | 0.838 | 0.781 | 0.897 | 0.674 | 0.76 | 0.678 | 0.73 | 0.794 | 0.778 | 0.714 | 0.657 | 0.652 | 0.659 | 0.73 | 0.77 | 0.675 | 0.684 | 0.69 | 0.76 | 0.727 | 0.675 | 0.695 | 0.842 | 0.879 | 0.791 | 0.75 | 0.758 | 23.444 | 0.75626 | 0.897 | 3.53
February | 0.765 | 0.828 | 0.816 | 0.788 | 0.746 | 0.767 | 0.745 | 0.827 | 0.831 | 0.855 | 0.824 | 0.783 | 0.844 | 0.809 | 0.801 | 0.884 | 0.835 | 0.903 | 0.823 | 0.871 | 0.869 | 0.857 | 0.896 | 0.864 | 0.829 | 1.255 | 1.053 | 1.058 |  |  |  | 24.026 | 0.85807 | 1.255 | 4.52
March | 0.999 | 1.004 | 0.975 | 1.176 | 0.994 | 0.924 | 0.895 | 0.898 | 1.008 | 0.931 | 0.906 | 0.889 | 0.879 | 0.898 | 0.871 | 0.842 | 0.816 | 0.785 | 0.767 | 0.788 | 0.807 | 0.802 | 0.793 | 0.824 | 0.845 | 0.807 | 0.779 | 0.799 | 0.779 | 0.808 | 0.811 | 27.099 | 0.87416 | 1.176 | 1.61
April | 0.763 | 0.776 | 0.748 | 0.807 | 0.845 | 0.869 | 0.868 | 0.81 | 0.802 | 0.791 | 0.795 | 0.787 | 0.833 | 0.877 | 0.717 | 0.77 | 0.802 | 0.763 | 0.833 | 0.804 | 0.749 | 0.758 | 0.771 | 0.909 | 0.603 | 0.76 | 0.747 | 0.758 | 0.742 | 0.772 |  | 23.629 | 0.78763 | 0.909 | 3.47
May | 0.752 | 0.769 | 0.747 | 0.777 | 0.757 | 0.755 | 0.715 | 0.748 | 0.745 | 0.743 | 0.777 | 0.784 | 0.801 | 0.89 | 0.746 | 0.778 | 0.746 | 0.795 | 0.782 | 0.768 | 0.759 | 0.744 | 0.734 | 0.76 | 0.788 | 0.718 | 0.795 | 0.769 | 0.78 | 0.747 | 0.741 | 23.71 | 0.76484 | 0.89 | 2.27
June | 0.745 | 0.742 | 0.809 | 0.682 | 0.734 | 0.709 | 0.739 | 0.836 | 0.875 | 1.092 | 1.009 | 0.976 | 1.102 | 1.091 | 1.145 | 1.114 | 1.151 | 1.252 | 1.908 | 1.936 | 1.308 | 1.182 | 1.133 | 1.029 | 0.98 | 1.018 | 1.006 | 1.003 | 0.995 | 0.959 |  | 31.26 | 1.042 | 1.936 | 12.66
July | 0.951 | 0.884 | 0.879 | 0.947 | 0.952 | 0.986 | 0.988 | 1.416 | 1.571 | 1.632 | 1.375 | 1.508 | 1.501 | 1.338 | 1.144 | 1.188 | 1.126 | 1.103 | 1.162 | 1.325 | 1.18 | 1.109 | 1.067 | 1.277 | 1.861 | 1.765 | 1.604 | 1.409 | 1.323 | 1.269 | 1.289 | 39.129 | 1.2622 | 1.861 | 14.68
August | 1.277 | 1.197 | 1.163 | 1.115 | 1.17 | 1.079 | 1.019 | 1.042 | 0.994 | 1.006 | 0.961 | 0.928 | 0.94 | 1.519 | 1.756 | 1.944 | 1.873 | 1.58 | 1.395 | 1.335 | 1.318 | 1.228 | 1.195 | 1.144 | 1.096 | 1.029 | 1.009 | 1.011 | 0.939 | 1.028 | 1.105 | 37.395 | 1.2063 | 1.944 | 8.57
September | 1.016 | 1.095 | 1.151 | 1.084 | 1.033 | 0.988 | 0.959 | 0.94 | 0.946 | 0.924 | 0.9 | 0.868 | 0.846 | 0.905 | 0.999 | 0.967 | 0.945 | 0.86 | 0.835 | 0.846 | 0.846 | 0.802 | 0.768 | 0.786 | 0.778 | 0.776 | 0.771 | 0.782 | 0.8 | 0.779 |  | 26.995 | 0.89983 | 1.151 | 2.34
October | 0.767 | 0.761 | 0.771 | 0.741 | 0.766 | 0.758 | 0.745 | 0.798 | 0.789 | 0.746 | 0.734 | 0.74 | 0.714 | 0.712 | 0.719 | 0.717 | 0.686 | 0.963 | 1.38 | 1.107 | 1.017 | 0.973 | 0.849 | 0.994 | 1.066 | 1.03 | 1.003 | 0.963 | 0.886 | 0.883 | 0.858 | 26.636 | 0.85923 | 1.38
November | 0.826 | 0.809 | 0.814 | 0.783 | 0.808 | 0.775 | 0.835 | 0.829 | 0.957 | 0.719 | 0.777 | 0.717 | 0.713 | 0.738 | 0.691 | 0.654 | 0.705 | 0.682 | 0.669 | 0.677 | 0.673 | 0.691 | 0.739 | 0.665 | 0.642 | 0.69 | 0.734 | 0.662 | 0.646 | 0.711 |  | 22.031 | 0.73437 | 0.957 | 0.84
December | 0.735 | 0.633 | 0.606 | 0.628 | 0.644 | 0.627 | 0.71 | 0.708 | 0.711 | 0.719 | 0.691 | 0.851 | 0.579 | 0.678 | 0.717 | 0.714 | 0.814 | 0.689 | 0.682 | 0.734 | 0.753 | 0.912 | 1.213 | 0.991 | 0.881 | 0.917 | 0.873 | 0.919 | 0.911 | 0.835 | 0.796 | 23.871 | 0.77003 | 1.213 | 4.86
FLW-1
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
11 |  | 0
12 |  | 0
13 |  | 0
14 |  | 0
15 |  | 0
16 |  | 0
17 |  | 0
18 |  | 0
19 |  | 0
20 |  | 0
21 |  | 0
22 |  | 0
23 |  | 0
24 |  | 0
25 |  | 0
26 |  | 0
27 |  | 0
28 |  | 0
29 |  | 0
30 |  | 0
31 |  | 0
| 0 | 0