## Sanlando-Wekiva
255/368 Wekiva 2019
Operating Permit No.: |  | FL0036251 |  |  | Expires: | 2021-03-30
Plant Permitted Capacity |  | 2.900 mgd AADF
Perc Ponds |  | 0.400 mgd
Reuse/Public Access |  | 2.603 mgd | [5 empty] | From Historical Data
Surface Discharge |  | 0.870 mgd AADF | [5 empty] | From Daily Flow Worksheet
Manual Data entry from DMR
Hyperlinks!A1
Go to Central Fl Operations/Sanlando/Wekiva/W
FLW-4
Sweetwater | Plant Flow (FLW-1) |  |  |  | Surface Discharge Flow (FLW-4) D-001 |  |  |  |  | CBOD5 |  | TSS |  | pH |  | Fecal Coliform |  |  | TRC |  | Nitrogen/Ammonia |  | Nitrogen | Nitrate | Phosphorus |  | Dissolved Oxygen
| Mo Flow | An. Avg | Mo Avg | Peak | Mo Flow | An. Avg | Mo Avg | Peak | % Of | Mo Avg | Max | Mo Avg | Max | Min | Max | An Avg | MoGeoMean | Max | Min | Max | Mo Avg | Max | Mo Avg | Max. | Mo Avg | Max | Min
| mgd | mgd | mgd | mgd | mgd | mgd | mgd | mgd | Flow | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | #/100ml | #/100ml | #/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
Limit | Total | 2.9 | Report |  | Total | 0.87 | Report |  | To D-1 | 5 | 6 | 5 | 6 | 6 | 8.5 | 200 | Report | 800 | 0.5 | 0.01 | 2.5 | 3 |  |  | 0.4 | 0.5 | 6
2019-01-01 | 59.867 | 1.716 | 1.9312 | 2.504 | 3.118 | 0.156 | 0.10058 | 1.267 |  | <2.0 | <2.0 | 0.9 | 1.8 | 6.8 | 7.5 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.3 | 0.5 | 1.1 | 2 | 0.2 | 0.5 | 8.5
February | 55.572 | 1.675 | 1.9847 | 2.421 | 3.046 | 0.13 | 0.10879 | 1.267 |  | <2.0 | <2.0 | <1.0 | <1.0 | 6 | 7.5 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.9 | 0.9 | 1.6 | 0.5 | 0.1 | 0.1 | 7.1
March | 52.198 | 1.78 | 1.6838 | 3.246 | 7.043 | 0.15 | 0.22719 | 2.157 |  | <2.0 | <2.0 | 3.6 | 6 | 6 | 7.6 | <1.0 | <1.0 | <1.0 | 0.6 | 0.01 | 0.5 | 0.9 | 1.2 | 1.4 | 0.4 | 0.5 | 7.4
April | 46.289 | 1.825 | 1.543 | 2.115 | 1.244 | 0.542 | 0.041467 | 0.512 |  | <2.0 | <2.0 | <1.0 | 1.4 | 6.3 | 7.8 | <1.0 | <1.0 | <1.0 | 0.6 | 0 | 2.3 | 3 | 2.2 | 0.54 | 0.4 | 0.5 | 7.2
May | 56.844 | 1.853 | 1.8337 | 2.778 | 0.719 | 0.544 | 0.023194 | 0.244 |  | <2.0 | <2.0 | 2.3 | 6 | 6 | 7.5 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 1.3 | 1.9 | 1.8 | 0.97 | 0.3 | 0.5 | 7.7
June | 63.143 | 1.897 | 2.1048 | 2.918 | 7.71 | 0.565 | 0.257 | 2.125 |  | <2.0 | <2.0 | <1.0 | <1.0 | 6 | 7.5 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.1 | 0.3 | 0.8 | 1.8 | 0.4 | 0.5 | 7.1
July | 63.306 | 1.936 | 2.0421 | 2.674 | 11.73 | 0.595 | 0.37839 | 2.331 |  | <2.0 | <2.0 | <1.0 | <1.0 | 6.1 | 7.7 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.9 | 2.2 | 3.8 | 3.3 | 0.4 | 0.5 | 6.6
August | 75.897 | 2.006 | 2.4483 | 3.482 | 10.568 | 0.623 | 0.3409 | 2.671 |  | 2.5 | 5.6 | <1.0 | <1.0 | 6.2 | 7.5 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.9 | 2.6 | 4.4 | 4 | 0.4 | 0.4 | 6.7
September | 58.352 | 1.98 | 1.9451 | 3.671 | 2.549 | 0.562 | 0.084967 | 0.757 |  | <2.0 | <2.0 | 1.6 | 2.8 | 6.6 | 7.8 | <1.0 | <1.0 | <1.0 | 0.5 | 0.01 | 0.6 | 1.9 | 7.3 | 11 | 0.4 | 0.5 | 6.9
October | 63.876 | 1.98 | 2.0605 | 2.682 | 4.574 | 0.496 | 0.14755 | 2.504 |  | <2.0 | <2.0 | 1.8 | 3.2 | 6.3 | 7.8 | <1.0 | <1.0 | <1.0 | 1 | 0.01 | 0.1 | 0.2 | 8.3 | 12 | 0.3 | 0.3 | 6.7
November | 60.259 | 1.986 | 2.0086 | 2.369 | 1.308 | 0.334 | 0.0436 | 0.244 |  | <2.0 | <2.0 | <1.0 | <1.0 | 6.4 | 7.5 | <1.0 | <1.0 | 2 | 1 | 0 | 0.58 | 1.7 | 7.5 | 10 | 0.4 | 0.5 | 7
December | 56.49 | 1.955 | 1.8223 | 3.301 | 8.409 | 0.198 | 0.27126 | 1.82 |  | 3.1 | 6 | 3.1 | 5.6 | 6.6 | 7.7 | <1.0 | 1.5 | 10 | 1 | 0.01 | 0.5 | 1.6 | 8.1 | 10 | 0.4 | 0.5 | 7
Total | 712.093 |  |  |  | 62.018
Average |  | 1.8824 | 1.9507 | 2.8467 | 5.1682 | 0.40792 | 0.16874 | 1.4916 |  | 2.8 | 5.8 | 2.2167 | 3.8286 | 6.275 | 7.6167 |  | 1.5 | 6 | 0.64167 | 0.0083333 | 0.74833 | 1.475 | 4.0083 | 4.7925 | 0.34167 | 0.44167 | 7.1583
Minimum |  | 1.675 | 1.543 |  |  | 0.13 | 0.023194 |  |  | 2.5 |  | 0.9 |  | 6 |  | 0 | 1.5 |  | 0.5 |  | 0.1 |  | 0.8 | 0.5 | 0.1 |  | 6.6
Maximum |  | 2.006 | 2.4483 | 3.671 |  | 0.623 | 0.37839 | 2.671 |  | 3.1 | 6 | 3.6 | 6 |  | 7.8 | 0 | 1.5 | 10 |  |  | 2.3 | 3 | 8.3 | 12 | 0.4 | 0.5
FLW-2
RIBS | Flow (FLW-2) RIBS |  |  |  | CBOD5 |  |  | TSS |  |  | pH |  | Fecal Coliform |  |  | TRC | Nitrate
| Mo Flow | An Avg | Mo Avg | Peak | An. Avg | Mo. Avg. | Max | An. Avg. | Mo. Avg. | Max | Min | Max | An. Avg. | Mo.Geo | Max | Min | Max
| mgd | mgd | mgd | mgd | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | #/100ml | #/100ml | #/100ml | mg/L | mg/L
Limit | Total | 0.4 | Report |  | 20 | 30 | 60 | 20 | 30 | 60 | 6 | 8.5 | 200 | Report | 800 | 0.5 | 12
2019-01-01 | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
February | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
March | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
April | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
May | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
June | 0 | NOD | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
July | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
August | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
September | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
October | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
November | 0 | 0 | 0 | 0 | 0 | NOD | NOD | 0 | NOD | NOD | NOD | NOD | 0 | NOD | NOD | NOD | NOD
December | 0.16 | 0 | 0.0051613 | 0.16 | 1 | NOD | NOD | 1 | NOD | NOD | NOD | NOD | 1 | NOD | NOD | NOD | NOD
Total | 0
Average |  | 0
Minimum |  | 0 | 0 |  | 0 |  |  | 0 |  |  |  |  | 0
Maximum |  | 0 | 0.0051613 | 0.16 | 1 | 0 | 0 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 |  | 0
FLW-3
Reclaimed | Flow (FLW-3) Reclaimed |  |  |  | CBOD5 |  |  | TSS | pH |  | Fecal Coliform |  | TRC
| Mo Flow | An Avg | Mo Avg | Peak | An. Avg | Mo. Avg. | Max | Max | Min | Max | 75% Min. | Max | Min
| mgd | mgd | mgd | mgd | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | #/100ml | #/100ml | mg/L
Limit | Total | 2.9 | Report |  | 20 | 30 | 60 | 5 | 6 | 8.5 | ND | 25 | 1
2019-01-01 | 76.877 | 1.93 | 2.4799 | 4.311 | <2.0 | <2.0 | <2.0 | <1 | 6.7 | 7.8 | 100% | <1 | 1
February | 67.636 | 1.928 | 2.4156 | 4.311 | <2.0 | <2.0 | <2.0 | <1 | 6.8 | 7.2 | 100% | <1.0 | 1
March | 61.039 | 2.077 | 1.969 | 5.542 | <2.0 | <2.0 | 3 | <1 | 6.6 | 8 | 100% | <1.0 | 1
April | 57.946 | 2.126 | 1.9315 | 3.58 | <2.0 | 2.6 | 4.9 | 5 | 6.5 | 7.8 | 100% | <1 | 1
May | 75.868 | 2.208 | 2.4474 | 5.289 | <2.0 | <2.0 | <2.0 | <1 | 6.3 | 8.5 | 100% | <1.0 | 1
June | 70.973 | 2.262 | 2.3658 | 3.031 | <2.0 | <2.0 | <2.0 | 5 | 6.5 | 8 | 100% | <1.0 | 1
July | 74.537 | 2.305 | 2.4044 | 8.562 | <2.0 | <2.0 | 2.4 | 5 | 6.7 | 8.3 | 100% | <1.0 | 1
August | 75.344 | 2.311 | 2.4305 | 4.602 | <2.0 | <2.0 | <2.0 | <1 | 6.4 | 7.8 | 100% | <1.0 | 1
September | 60.552 | 2.284 | 2.0184 | 3.184 | <2.0 | <2.0 | <2.0 | <1 | 6.7 | 8 | 100% | <1.0 | 1
October | 78.838 | 2.308 | 2.5432 | 4.59 | <2.0 | <2.0 | <2.0 | <1.0 | 6.5 | 8.1 | 100% | <1.0 | 1
November | 73.372 | 2.316 | 2.4457 | 2.97 | <2.0 | 2.6 | 7.5 | <1.0 | 6.2 | 8.4 | 100% | <1.0 | 1
December | 63.377 | 2.312 | 2.0444 | 5.638 | <2.0 | 3..3 | 10 | 5 | 6.3 | 8.2 | 100% | <1.0 | 1
Total | 836.359
Average |  | 2.1972 | 2.2913 | 4.6342 |  | 2.6 | 5.56 | 5 | 6.5167 | 8.0083 | 1 |  | 1
Minimum |  | 1.928 | 1.9315 |  | 0 | 2.6 | 2.4 | 5 | 6.2 |  | 1 |  | 1
Maximum |  | 2.316 | 2.5432 | 8.562 | 0 | 2.6 | 10 | 5 |  | 8.5 | 1 | 0
Historical Data
| Plant FLW-1 | PltFlow FLW-1 | Ribs | Ribs | Ribs | Reuse | Reuse | Reuse | Rib+Reuse | R+R |  | RAA
| Avg. Flow | 3MoAvg | Mo.Avg.Flow | 3MoAvg | RAA | Mo.Avg.Flow | 3MoAvg | RAA | MoAvg | RAA |  | Reuse%
2018-01-01 | 2.0135 | 1.8645 | 0 | 0.0086722 | 0.18458 | 1.5835 | 1.3317 | 1.149 | 1.5835 | 0.19889 |  | 160.9% | 2018-01-18
February | 1.3554 | 1.6288 | 0 | 0 | 0.15867 | 1.2194 | 1.4357 | 1.1727 | 1.2194 | 0.19815 |  | 148.5% | 2018-02-18
March | 1.1746 | 1.5145 | 0 | 0 | 0.13653 | 1.4807 | 1.4279 | 1.2419 | 1.4807 | 0.19498 |  | 136.2% | 2018-03-18 |  | Jacquee
April | 1.2721 | 1.2674 | 0 | 0 | 0.11294 | 1.5554 | 1.4185 | 1.2912 | 1.5554 | 0.18905 |  | 136.4% | Apl 18 |  | 1 | Copy/Paste Value' the 2018 Historical Data from the 2018 DMR Summaries workbook.
May | 1.5127 | 1.3198 | 0 | 0 | 0.098811 | 1.4657 | 1.5006 | 1.2988 | 1.4657 | 0.18187 |  | 139.9% | 2018-05-18 |  | 2 | Enter in the formulas/links into the 2019 Table below and also the formulas in row 36
June | 1.5698 | 1.4515 | 0 | 0 | 0.073083 | 1.7145 | 1.5785 | 1.2787 | 1.7145 | 0.17137 |  | 140.4% | 2018-06-18
July | 1.6112 | 1.5646 | 0 | 0 | 0.051116 | 1.8922 | 1.6908 | 1.2864 | 1.8922 | 0.15805 |  | 133.4% | 2018-07-18
August | 1.2721 | 1.4844 | 0 | 0 | 0.025884 | 1.5554 | 1.7207 | 1.2945 | 1.5554 | 0.14143 |  | 131.3% | 2018-08-18
September | 2.0691 | 1.6508 | 0 | 0 | 0.011026 | 2.3489 | 1.9322 | 1.3619 | 2.3489 | 0.12346 |  | 111.8% | 2018-09-18
October | 1.868 | 1.7364 | 0 | 0 | 0.0040867 | 2.2491 | 2.0511 | 1.4599 | 2.2491 | 0.10548 |  | 99.09% | 2018-10-18
November | 1.6997 | 1.8789 | 0 | 0 | 0.0014454 | 2.1422 | 2.2467 | 1.6065 | 2.1422 | 0.088069 |  | 91.43% | 2018-11-18
December | 1.8481 | 1.8053 | 0 | 0 | 0.00072269 | 2.1003 | 2.1639 | 1.7082 | 2.1003 | 0.071574 |  | 90.42% | 2018-12-18
2019-01-01 | 1.9312 | 1.8263 | 0 | 0 | 0 | 2.4799 | 2.2408 | 1.784 | 2.4799 | 0.056193 |  | 86.4% | 2019-01-19
February | 1.9847 | 1.9213 | 0 | 0 | 0 | 2.4156 | 2.3319 | 1.8586 | 2.4156 | 0.04297 |  | 84.67% | 2019-02-19
March | 1.6838 | 1.8666 | 0 | 0 | 0 | 1.969 | 2.2882 | 1.9303 | 1.969 | 0.031593 |  | 85.07% | 2019-03-19
April | 1.543 | 1.7372 | 0 | 0 | 0 | 1.9315 | 2.1054 | 1.9876 | 1.9315 | 0.022181 |  | 84.87% | Apl 19
May | 1.8337 | 1.6868 | 0 | 0 | 0 | 2.4474 | 2.116 | 2.0388 | 2.4474 | 0.013947 |  | 82.84% | 2019-05-19
June | 2.1048 | 1.8271 | 0 | 0 | 0 | 2.3658 | 2.2482 | 2.0947 | 2.3658 | 0.0078567 |  | 82.82% | 2019-06-19
July | 2.0421 | 1.9935 | 0 | 0 | 0 | 2.4044 | 2.4058 | 2.1542 | 2.4044 | 0.0035971 |  | 82.85% | 2019-07-19
August | 2.4483 | 2.1984 | 0 | 0 | 0 | 2.4305 | 2.4002 | 2.2109 | 2.4305 | 0.00144 |  | 84.5% | 2019-08-19
September | 1.9451 | 2.1452 | 0 | 0 | 0 | 2.0184 | 2.2844 | 2.2402 | 2.0184 | 0.00052123 |  | 85.08% | 2019-09-19
October | 2.0605 | 2.1513 | 0 | 0 | 0 | 2.5432 | 2.3307 | 2.2635 | 2.5432 | 0.00018067 |  | 84.87% | 2019-10-19
November | 2.0086 | 2.0047 | 0.0051613 | 0.0017204 | 0.00014337 | 2.4457 | 2.3358 | 2.2709 | 2.4509 | 7.2171e-05 |  | 85.05% | 2019-11-19
December | 1.8223 | 1.9638 | 0 | 0.0017204 | 0.00028674 | 2.0444 | 2.3444 | 2.286 | 2.0444 | 3.5842e-05 |  | 85.13% | 2019-12-19
Note on C12: From page 3 of DMR 'Flow (total through plant) PARM Code 50050 FLW-1'
Note on G12: From page 3 of DMR 'Flow (Surface water discharge) ARM Code 50050 FLW-4'
Note on F33: From page 4 of DMR 'BOD, Carbonaceous 5 day, 20C EFA-1
Note on I33: From page 4 of the DMR 'Solids, Total Suspended PARM Code 00530 EFA-1'
Note on L33: From page 5 of the DMR 'pH PARM Code 00400 EFA-1'
Note on N33: From page 5 of the DMR 'Coliform, Fecal PARM Code 74055 EFA-1'
Note on Q33: From page 5 of the DMR 'Total Residual Chlorine (For Disinfection) PARM Code 50060 EFA-1'
Note on R33: From page 5 of the DMR 'Nitrogen, Nitrate, Total (as N) PARM Code 00620 EFA-1'
Note on C34: Annual Flow
Note on F55: From page 6 of the DMR 'BOD, Carbonaceous 5 day, 20C PARM Code 80082 EFA-1
Note on I55: From page 6 of the DMR 'Solids, Total Suspended PARM Code 00530 EFB-1'
Note on J55: From page 6 of the DMR 'pH PARM Code 00400 EFA-1'
Note on N55: From page 7 of the DMR 'Total Residual Chlorine (For Disinfection) PARM Code 50060 EFA-1'
Note on L56: From page 8 of the DMR 'Coliform, Fecal, %less than detection PARMCode 51005 EFA-1'
Note on M56: From page 7 of the DMR 'Coliform, Fecal PARM Code 74055 EFA-1'

## Wekiva Flow Summary
2019 Sanlando - Wekiva DMR Flow Summary
[7 empty] | Hyperlinks!A1 |  |  | Note: Daily flows can be pulled from |  |  |  | \uiwater.com\files\Operations\Operations Files\Southeast\Florida\Central FL Operations\Sanlando\Wekiva\2015 PLANT READS\Wekiva 2016 STP Reads
Copy Paste Special-Value-Transpose to applicable FLW
Wekiva FLW-1 (Flow Total Through Plant at EFA-1) | [31 empty] | Wekiva FLW-1 (Flow Total Through Plant at EFA-1)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 2.312 | 1.999 | 2.192 | 2.248 | 1.892 | 2.082 | 2.149 | 2.246 | 2.058 | 1.475 | 0.733 | 0.913 | 1.194 | 1.967 | 2.155 | 2.039 | 1.69 | 1.939 | 2.14 | 2.014 | 1.409 | 2.038 | 2.111 | 1.98 | 2.047 | 1.952 | 1.99 | 1.754 | 2.504 | 2.364 | 2.281 | 59.867 | 1.9312 | 2.504
February | 2.27 | 2.044 | 2.178 | 0.911 | 1.262 | 1.485 | 2.064 | 2.14 | 2.018 | 2.003 | 2.061 | 2.261 | 2.421 | 1.89 | 2.182 | 2.159 | 2.064 | 1.351 | 2.128 | 2.052 | 1.969 | 2.154 | 2.045 | 2.353 | 1.83 | 2.153 | 2.077 | 2.047 |  |  |  | 55.572 | 1.9847 | 2.421
March | 2.056 | 1.942 | 2.018 | 1.88 | 2.061 | 1.978 | 1.903 | 2.168 | 1.958 | 1.835 | 2.026 | 2.059 | 2.101 | 1.701 | 2.003 | 1.888 | 1.911 | 1.723 | 0.653 | 0.91 | 0.534 | 1.063 | 0.974 | 0 | 1.49 | 1.8 | 1.501 | 1.358 | 1.82 | 1.638 | 3.246 | 52.198 | 1.6838 | 3.246
April | 2.06 | 1.45 | 1.822 | 1.843 | 2.004 | 1.89 | 0.962 | 0.783 | 1.557 | 2.025 | 1.969 | 2.115 | 1.951 | 1.372 | 0.45 | 1.472 | 1.374 | 1.804 | 1.811 | 1.854 | 1.795 | 1.969 | 1.094 | 1.998 | 0.937 | 0.335 | 1.133 | 1.444 | 1.727 | 1.289 |  | 46.289 | 1.543 | 2.115
May | 1.562 | 1.243 | 2.778 | 1.765 | 2.384 | 2.149 | 1.516 | 1.216 | 2.266 | 1.672 | 2.28 | 1.724 | 1.931 | 2.168 | 1.964 | 1.899 | 1.908 | 1.862 | 1.89 | 1.972 | 1.993 | 0 | 1.793 | 1.808 | 1.803 | 1.983 | 1.96 | 1.832 | 1.896 | 1.706 | 1.921 | 56.844 | 1.8337 | 2.778
June | 1.94 | 1.662 | 1.851 | 1.938 | 1.78 | 2.057 | 1.989 | 1.941 | 1.856 | 2.038 | 2.25 | 2.093 | 2.148 | 2.398 | 1.639 | 2.918 | 2.353 | 2.509 | 2.47 | 2.611 | 2.084 | 1.499 | 2.128 | 2.145 | 2.176 | 2.185 | 2.029 | 2.12 | 2.098 | 2.238 |  | 63.143 | 2.1048 | 2.918
July | 1.448 | 1.765 | 1.527 | 1.399 | 1.604 | 1.67 | 1.886 | 2.085 | 2.236 | 0 | 2.334 | 2.354 | 2.168 | 2.168 | 2.164 | 2.123 | 2.079 | 2.167 | 2.586 | 2.219 | 2.387 | 2.018 | 2.674 | 2.076 | 1.863 | 2.297 | 2.348 | 2.276 | 2.564 | 2.412 | 2.409 | 63.306 | 2.0421 | 2.674
August | 3.482 | 2.673 | 2.943 | 2.939 | 2.942 | 2.82 | 2.664 | 2.411 | 2.285 | 2.827 | 2.453 | 2.48 | 2.376 | 2.633 | 2.633 | 2.369 | 2.363 | 2.659 | 2.499 | 2.495 | 2.4 | 2.304 | 2.245 | 1.134 | 1.641 | 1.953 | 2.096 | 2.245 | 2.262 | 2.39 | 2.281 | 75.897 | 2.4483 | 3.482
September | 2.227 | 1.694 | 1.826 | 2.267 | 1.427 | 1.998 | 2.365 | 1.655 | 2.26 | 3.671 | 0.857 | 1.892 | 2.412 | 1.776 | 1.546 | 2.413 | 2.326 | 2.109 | 2.016 | 1.823 | 1.16 | 1.476 | 2.108 | 1.778 | 1.919 | 1.499 | 2.278 | 1.836 | 1.798 | 1.94 |  | 58.352 | 1.9451 | 3.671
October | 2.421 | 2.06 | 1.776 | 1.811 | 1.673 | 1.644 | 1.874 | 2.214 | 1.802 | 1.882 | 1.685 | 1.928 | 1.562 | 1.973 | 1.86 | 2.188 | 2.081 | 1.615 | 1.827 | 2.518 | 2.473 | 2.682 | 2.43 | 2.091 | 2.419 | 2.422 | 2.207 | 2.355 | 2.305 | 2.251 | 1.847 | 63.876 | 2.0605 | 2.682
November | 2.027 | 2.103 | 2.035 | 2.055 | 2.171 | 2.121 | 2.051 | 2.09 | 1.927 | 1.975 | 2.103 | 2.369 | 2.026 | 1.694 | 2.025 | 2.07 | 1.842 | 2.025 | 2.043 | 2.043 | 1.959 | 1.956 | 1.921 | 2.042 | 1.952 | 1.925 | 1.901 | 1.716 | 2.003 | 2.089 |  | 60.259 | 2.0086 | 2.369
December | 1.814 | 1.584 | 1.752 | 1.895 | 1.78 | 1.842 | 1.895 | 1.9 | 1.978 | 1.889 | 1.663 | 1.849 | 2.074 | 2.023 | 2.005 | 1.873 | 1.029 | 1.877 | 1.32 | 1.685 | 1.614 | 1.661 | 1.183 | 1.409 | 1.66 | 1.314 | 1.739 | 2.185 | 3.301 | 2.33 | 2.367 | 56.49 | 1.8223 | 3.301
Wekiva FLW-2 (Flow Percolation Ponds R-001)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
December | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.0051613 | 0.16
Wekiva FLW-3 (Flow Public Access Irrigation R-002) | [31 empty] | Wekiva FLW-3 (Flow Public Access Irrigation R-002)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 2.099 | 2.003 | 4.311 | 3.587 | 3.41 | 1.962 | 1.828 | 2.821 | 2.971 | 2.999 | 2.817 | 0.682 | 0.55 | 0.532 | 0.514 | 3.526 | 4.078 | 2.509 | 2.267 | 2.261 | 0.125 | 4.087 | 2.17 | 2.001 | 3.557 | 3.748 | 2.177 | 2.044 | 1.991 | 3.629 | 3.621 | 76.877 | 2.4799 | 4.311
February | 2.099 | 2.003 | 4.311 | 3.587 | 3.41 | 1.962 | 1.828 | 2.821 | 2.971 | 2.999 | 2.817 | 0.682 | 0.55 | 0.532 | 0.514 | 3.526 | 4.078 | 2.509 | 2.267 | 2.261 | 0.125 | 4.087 | 2.17 | 2.001 | 3.557 | 3.748 | 2.177 | 2.044 |  |  |  | 67.636 | 2.4156 | 4.311
March | 3.798 | 0.491 | 0.682 | 3.001 | 2.297 | 3.586 | 3.144 | 3.344 | 2.009 | 1.588 | 0.815 | 2.724 | 0.606 | 2.199 | 2.743 | 2.426 | 2.19 | 2.412 | 2.193 | 1.831 | 0.845 | 0.689 | 0.607 | 0.59 | 2.669 | 2.924 | 0.614 | 0.678 | 0.909 | 0.893 | 5.542 | 61.039 | 1.969 | 5.542
April | 2.291 | 1.488 | 2.549 | 2.096 | 2.145 | 2.36 | 1.656 | 2.062 | 0.457 | 2.63 | 2.885 | 3.58 | 3.407 | 2.513 | 0.709 | 0.648 | 0.636 | 2.532 | 2.676 | 2.308 | 0.647 | 3.196 | 2.79 | 1.702 | 0.693 | 0.705 | 0.672 | 0.735 | 2.635 | 2.543 |  | 57.946 | 1.9315 | 3.58
May | 2.689 | 2.667 | 2.673 | 2.583 | 2.617 | 2.312 | 2.354 | 2.629 | 2.68 | 2.096 | 1.967 | 1.983 | 1.899 | 1.682 | 2.663 | 3.244 | 3.315 | 3.294 | 1.216 | 1.936 | 2.746 | 2.325 | 3.772 | 2.33 | 1.882 | 1.734 | 1.891 | 1.747 | 3.112 | 0.541 | 5.289 | 75.868 | 2.4474 | 5.289
June | 1.99 | 2.146 | 2.077 | 2.232 | 1.677 | 2.795 | 2.744 | 2.402 | 2.447 | 2.478 | 2.417 | 2.464 | 2.44 | 2.39 | 1.826 | 1.764 | 1.844 | 1.861 | 2.155 | 2.458 | 2.142 | 2.431 | 2.437 | 2.73 | 2.785 | 2.76 | 2.874 | 2.539 | 2.637 | 3.031 |  | 70.973 | 2.3658 | 3.031
July | 0.966 | 2.811 | 2.979 | 2.763 | 1.086 | 0.315 | 1.128 | 2.375 | 2.398 | 2.337 | 2.81 | 2.734 | 2.673 | 2.452 | 2.692 | 2.69 | 2.889 | 2.502 | 0.006 | 2.752 | 2.256 | 2.37 | 2.848 | 2.583 | 2.493 | 2.529 | 2.451 | 2.485 | 8.562 | 0.126 | 2.476 | 74.537 | 2.4044 | 8.562
August | 1.719 | 2.196 | 2.277 | 2.314 | 2.302 | 2.496 | 2.295 | 2.407 | 1.623 | 2.231 | 2.264 | 2.285 | 2.406 | 2.445 | 2.731 | 2.348 | 2.798 | 2.47 | 3.811 | 2.277 | 2.673 | 0.976 | 4.602 | 2.758 | 1.092 | 0.721 | 3.71 | 4.187 | 3.428 | 3.257 | 0.245 | 75.344 | 2.4305 | 4.602
September | 2.361 | 2.807 | 2.908 | 3.184 | 0 | 2.82 | 1.274 | 2.502 | 2.893 | 2.906 | 3.007 | 2.982 | 0.178 | 0.113 | 2.111 | 2.559 | 2.629 | 2.615 | 2.685 | 2.847 | 2.474 | 1.749 | 0.167 | 0.359 | 1.358 | 1.816 | 1.486 | 2.091 | 1.876 | 1.795 |  | 60.552 | 2.0184 | 3.184
October | 3.085 | 3.231 | 3.217 | 1.018 | 2.66 | 2.737 | 2.691 | 2.398 | 2.425 | 2.36 | 2.462 | 1.13 | 1.313 | 3.341 | 3.195 | 2.855 | 1.471 | 1.155 | 2.494 | 4.59 | 0.246 | 2.009 | 3.113 | 3.108 | 3.107 | 2.822 | 2.722 | 2.8 | 2.828 | 3.157 | 3.098 | 78.838 | 2.5432 | 4.59
November | 2.038 | 2.97 | 2.963 | 2.803 | 2.929 | 2.467 | 2.532 | 2.607 | 2.405 | 2.245 | 2.493 | 2.659 | 2.633 | 2.612 | 2.416 | 2.503 | 2.397 | 2.473 | 2.645 | 2.687 | 2.679 | 2.659 | 2.659 | 2.236 | 1.704 | 2.149 | 2.041 | 2.182 | 1.733 | 1.853 |  | 73.372 | 2.4457 | 2.97
December | 0.558 | 5.638 | 0.834 | 0.74 | 1.881 | 2.184 | 2.515 | 2.587 | 2.581 | 2.62 | 2.538 | 2.481 | 2.458 | 2.468 | 1.275 | 1.111 | 3.256 | 2.483 | 4.749 | 0 | 2.28 | 1.006 | 0.863 | 0.896 | 1.774 | 1.921 | 1.807 | 1.761 | 1.147 | 1.146 | 3.819 | 63.377 | 2.0444 | 5.638
Wekiva FLW-4 (Surface Water Discharge D-001) | [31 empty] | Wekiva FLW-4 (Surface Water Discharge D-001)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.238 | 0.088 | 0.376 | 0.042 | 0.031 | 0.708 | 1.267 | 0.203 | 0 | 0.042 | 0.019 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0.072 | 0 | 3.118 | 0.10058 | 1.267
February | 0 | 0 | 0 | 0 | 0 | 0 | 0.238 | 0.088 | 0.376 | 0.042 | 0.031 | 0.708 | 1.267 | 0.203 | 0 | 0.042 | 0.019 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 |  |  |  | 3.046 | 0.10879 | 1.267
March | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.742 | 0 | 0 | 2.157 | 1.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 1.781 | 0.157 | 0 | 0 | 0.181 | 7.043 | 0.22719 | 2.157
April | 0 | 0.237 | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0.512 | 0.078 | 0.08 | 0 | 0 | 0 | 0.244 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.244 | 0.041467 | 0.512
May | 0 | 0 | 0 | 0 | 0 | 0.244 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0.074 | 0 | 0 | 0 | 0.132 | 0.047 | 0 | 0 | 0.002 | 0.719 | 0.023194 | 0.244
June | 0.01 | 0.053 | 0 | 0 | 0 | 0.13 | 0.028 | 0 | 0 | 0.559 | 0 | 0 | 0 | 1.098 | 0.14 | 0 | 2.125 | 1 | 1.902 | 0.389 | 0 | 0.02 | 0.157 | 0.052 | 0 | 0 | 0.046 | 0.001 | 0 | 0 |  | 7.71 | 0.257 | 2.125
July | 0.761 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.651 | 1.278 | 0 | 0.033 | 0 | 0 | 1.873 | 0 | 0.228 | 0 | 2.157 | 0.063 | 0 | 0 | 0 | 0.285 | 0 | 0 | 1.962 | 0 | 2.331 | 0.001 | 0.057 | 11.73 | 0.37839 | 2.331
August | 0 | 0.002 | 1.705 | 0 | 2.671 | 0 | 0.948 | 0.002 | 1.459 | 0.3 | 0 | 0 | 0 | 1.135 | 0.505 | 0.474 | 0 | 0 | 0.792 | 0 | 0 | 0.333 | 0 | 0.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.568 | 0.3409 | 2.671
September | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0.389 | 0 | 0.707 | 0 | 0.346 | 0.757 | 0 | 0 | 0 | 0 | 0.166 |  | 2.549 | 0.084967 | 0.757
October | 0 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0.016 | 0.1 | 2.504 | 0 | 1.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.574 | 0.14755 | 2.504
November | 0 | 0 | 0 | 0 | 0 | 0.244 | 0.078 | 0.013 | 0 | 0 | 0.072 | 0 | 0 | 0.073 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.216 | 0.185 | 0 | 0.101 | 0.1 | 0.181 | 0 |  | 1.308 | 0.0436 | 0.244
December | 0 | 1.007 | 0 | 0.469 | 0.098 | 0.007 | 0.073 | 0 | 0 | 0 | 0 | 0.256 | 0 | 0.26 | 0 | 0 | 0 | 0 | 0.001 | 0.247 | 0 | 0 | 0.077 | 0 | 0.362 | 0 | 1.82 | 1.361 | 0.795 | 1.52 | 0.056 | 8.409 | 0.27126 | 1.82
Total Wekiva | [31 empty] | Wekiva Total Flow
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 4.411 | 4.002 | 6.503 | 5.835 | 5.302 | 4.044 | 3.977 | 5.067 | 5.029 | 4.474 | 3.55 | 1.595 | 1.744 | 2.499 | 2.669 | 5.565 | 5.768 | 4.448 | 4.407 | 4.275 | 1.534 | 6.125 | 4.281 | 3.981 | 5.604 | 5.7 | 4.167 | 3.798 | 4.495 | 5.993 | 5.902 | 136.744 | 4.4111 | 6.503
February | 4.369 | 4.047 | 6.489 | 4.498 | 4.672 | 3.447 | 3.892 | 4.961 | 4.989 | 5.002 | 4.878 | 2.943 | 2.971 | 2.422 | 2.696 | 5.685 | 6.142 | 3.86 | 4.395 | 4.313 | 2.094 | 6.241 | 4.215 | 4.354 | 5.387 | 5.901 | 4.254 | 4.091 |  |  |  | 123.208 | 4.4003 | 6.489
March | 5.854 | 2.433 | 2.7 | 4.881 | 4.358 | 5.564 | 5.047 | 5.512 | 3.967 | 3.423 | 2.841 | 4.783 | 2.707 | 3.9 | 4.746 | 4.314 | 4.101 | 4.135 | 2.846 | 2.741 | 1.379 | 1.752 | 1.581 | 0.59 | 4.159 | 4.724 | 2.115 | 2.036 | 2.729 | 2.531 | 8.788 | 113.237 | 3.6528 | 8.788
April | 4.351 | 2.938 | 4.371 | 3.939 | 4.149 | 4.25 | 2.618 | 2.845 | 2.014 | 4.655 | 4.854 | 5.695 | 5.358 | 3.885 | 1.159 | 2.12 | 2.01 | 4.336 | 4.487 | 4.162 | 2.442 | 5.165 | 3.884 | 3.7 | 1.63 | 1.04 | 1.805 | 2.179 | 4.362 | 3.832 |  | 104.235 | 3.4745 | 5.695
May | 4.251 | 3.91 | 5.451 | 4.348 | 5.001 | 4.461 | 3.87 | 3.845 | 4.946 | 3.768 | 4.247 | 3.707 | 3.83 | 3.85 | 4.627 | 5.143 | 5.223 | 5.156 | 3.106 | 3.908 | 4.739 | 2.325 | 5.565 | 4.138 | 3.685 | 3.717 | 3.851 | 3.579 | 5.008 | 2.247 | 7.21 | 132.712 | 4.281 | 7.21
June | 3.94 | 3.861 | 3.928 | 4.17 | 3.457 | 4.982 | 4.761 | 4.343 | 4.303 | 5.075 | 4.667 | 4.557 | 4.588 | 5.886 | 3.605 | 4.682 | 6.322 | 5.37 | 6.527 | 5.458 | 4.226 | 3.95 | 4.722 | 4.927 | 4.961 | 4.945 | 4.949 | 4.66 | 4.735 | 5.269 |  | 141.826 | 4.7275 | 6.527
July | 3.175 | 4.626 | 4.506 | 4.162 | 2.69 | 1.985 | 3.014 | 4.46 | 5.285 | 3.615 | 5.144 | 5.121 | 4.841 | 4.62 | 6.729 | 4.813 | 5.196 | 4.669 | 4.749 | 5.034 | 4.643 | 4.388 | 5.522 | 4.944 | 4.356 | 4.826 | 6.761 | 4.761 | 13.457 | 2.539 | 4.942 | 149.573 | 4.8249 | 13.457
August | 5.201 | 4.869 | 5.22 | 5.253 | 5.244 | 5.316 | 4.959 | 4.818 | 3.908 | 5.058 | 4.717 | 4.765 | 4.782 | 5.078 | 5.364 | 4.717 | 5.161 | 5.129 | 6.31 | 4.772 | 5.073 | 3.28 | 6.847 | 3.892 | 2.733 | 2.674 | 5.806 | 6.432 | 5.69 | 5.647 | 2.526 | 151.241 | 4.8787 | 6.847
September | 4.588 | 4.501 | 4.734 | 5.451 | 1.427 | 4.818 | 3.639 | 4.157 | 5.153 | 6.577 | 3.864 | 4.874 | 2.59 | 1.889 | 3.657 | 4.972 | 4.955 | 4.724 | 4.701 | 4.67 | 3.634 | 3.225 | 2.275 | 2.137 | 3.277 | 3.315 | 3.764 | 3.927 | 3.674 | 3.735 |  | 118.904 | 3.9635 | 6.577
October | 5.506 | 5.365 | 4.993 | 2.829 | 4.333 | 4.381 | 4.565 | 4.612 | 4.227 | 4.254 | 4.213 | 3.058 | 2.875 | 5.314 | 5.055 | 5.043 | 3.882 | 2.786 | 4.421 | 9.612 | 2.719 | 6.163 | 5.543 | 5.199 | 5.526 | 5.244 | 4.929 | 5.155 | 5.133 | 5.408 | 4.945 | 147.288 | 4.7512 | 9.612
November | 4.065 | 5.073 | 4.998 | 4.858 | 5.1 | 4.832 | 4.661 | 4.71 | 4.332 | 4.22 | 4.668 | 5.028 | 4.659 | 4.379 | 4.486 | 4.573 | 4.239 | 4.498 | 4.688 | 4.73 | 4.638 | 4.615 | 4.58 | 4.494 | 3.841 | 4.074 | 4.043 | 3.998 | 3.917 | 3.942 |  | 134.939 | 4.498 | 5.1
December | 2.372 | 7.382 | 2.586 | 2.635 | 3.661 | 4.026 | 4.41 | 4.487 | 4.559 | 4.509 | 4.201 | 4.33 | 4.532 | 4.491 | 3.28 | 2.984 | 4.285 | 4.36 | 6.069 | 1.685 | 3.894 | 2.667 | 2.046 | 2.305 | 3.434 | 3.235 | 3.546 | 3.946 | 4.448 | 3.476 | 6.186 | 120.027 | 3.8718 | 7.382
| FLW-1 | FLW-2 | FLW-3 | FLW-4 | Copy from Wekiva STP/DMRs (CntrlFl/Sanlando folder)
1 | 1.814 | 0 | 0.558 | 0
2 | 1.584 | 0.16 | 5.638 | 1.007
3 | 1.752 | 0 | 0.834 | 0
4 | 1.895 | 0 | 0.74 | 0.469
5 | 1.78 | 0 | 1.881 | 0.098
6 | 1.842 | 0 | 2.184 | 0.007
7 | 1.895 | 0 | 2.515 | 0.073
8 | 1.9 | 0 | 2.587 | 0
9 | 1.978 | 0 | 2.581 | 0
10 | 1.889 | 0 | 2.62 | 0
11 | 1.663 | 0 | 2.538 | 0
12 | 1.849 | 0 | 2.481 | 0.256
13 | 2.074 | 0 | 2.458 | 0
14 | 2.023 | 0 | 2.468 | 0.26
15 | 2.005 | 0 | 1.275 | 0
16 | 1.873 | 0 | 1.111 | 0
17 | 1.029 | 0 | 3.256 | 0
18 | 1.877 | 0 | 2.483 | 0
19 | 1.32 | 0 | 4.749 | 0.001
20 | 1.685 | 0 | 0 | 0.247
21 | 1.614 | 0 | 2.28 | 0
22 | 1.661 | 0 | 1.006 | 0
23 | 1.183 | 0 | 0.863 | 0.077
24 | 1.409 | 0 | 0.896 | 0
25 | 1.66 | 0 | 1.774 | 0.362
26 | 1.314 | 0 | 1.921 | 0
27 | 1.739 | 0 | 1.807 | 1.82
28 | 2.185 | 0 | 1.761 | 1.361
29 | 3.301 | 0 | 1.147 | 0.795
30 | 2.33 | 0 | 1.146 | 1.52
31 | 2.367 | 0 | 3.819 | 0.056
| 56.49 | 0.16 | 63.377 | 8.409